## Sheet1-IDU
Sr No | Set Point ID | Set Point Description | Default | Min | Max | Offset | Need to be stored in EEPROM | Resolution | Time Delay | Authorization Level
1 | ID0001 | IDU EXV | Free Run | 0 | 480 | 0 | Yes | 1 | 0 sec | R&D
2 | ID0002 | Tliq | Actual sensor value | -30 | 105 | 0 | Yes | 0.5 | 0 sec | R&D
3 | ID0003 | Tgas | Actual sensor value | -30 | 105 | 0 | Yes | 0.5 | 0 sec | R&D
4 | ID0004 | Room Temp | Actual sensor value | -30 | 105 | 0 | Yes | 0.5 | 0 sec | R&D
5 | ID0005 | Supply Temp | Actual sensor value | -30 | 105 | 0 | Yes | 0.5 | 0 sec | R&D
6 | ID0006 | DCL | 20 | 0 | 101 | 0 | Yes | 1 | 0 sec | R&D
7 | ID0007 | IDU Capacity | Preset | 0.5 | Free | 0 | Yes | 0.5 | 0 sec | R&D
8 | ID0008 | IDU Fan Step | Auto | 0-OFF | 5-Hi | 0 | Yes | 1 | 0 sec | R&D
9 | ID0009 | IDU Swing Position | 0- OFF | 0- OFF | 1- Swing | 0 | Yes | 1 | 0 sec | R&D
10 | ID0010 | Set Temp. | 27 | 16 | 32 | 0 | Yes | 1 | 0 sec | R&D
11 | ID0011 | Fire Input | 0-OFF | 0-OFF | 1-ON | 0 | Yes | 1 | 0 sec | R&D
12 | ID0012 | Door Input | 0-OFF | 0-OFF | 1-ON | 0 | Yes | 1 | 0 sec | R&D
13 | ID0013 | Shift Temp. | 0 | 0 | 10 | 0 | Yes | 1 | 0 sec | R&D
14 | ID0014 | Flaot Switch | 1-ON | 0-OFF | 1-ON | 0 | Yes | 1 | 0 sec | R&D
15 | ID0015 | Drain Pump | 1 | 0-OFF | 1-ON | 0 | Yes | 1 | 0 sec | R&D
16 | ID0016 | Drain Time Extension | 180 sec | 0 | 900 sec | 0 | Yes | 1 | 0 sec | R&D
17 | ID0017 | Drain ON Delay Time | 540 sec | 0 | 900 sec | 0 | Yes | 1 | 0 sec | R&D
18 | ID0018 | Tliq for Drain Pump | 2 | 0 | 5 | 0 | Yes | 0.5 | 0 sec | R&D
19 | ID0019 | DC pump low rpm | 100 | 0 | 500 | 0 | Yes | 1 | 0 sec | R&D
20 | ID0020 | DC pump low rpm time | 30 sec | 0 | 600 sec | 0 | Yes | 1 | 0 sec | R&D
21 | ID0021 | IDU Fan Stop Time | 60 sec | 0 | 180 sec | 0 | Yes | 1 | 0 sec | R&D
22 | ID0022 | IDU Fan Startup Time at Hi | 5 sec | 0 | 180 sec | 0 | Yes | 1 | 0 sec | R&D
23 | ID0023 | Fan Feedback Time | 5 sec | 0 | 180 sec | 0 | Yes | 1 | 0 sec | R&D
24 | ID0024 | Max Time Fan in Draft | 300 sec | 0 | 600 sec | 0 | Yes | 1 | 0 sec | R&D
25 | ID0025 | Tliq Temp H1 for Fan | <12 | -30 | 105 | 0 | Yes | 0.5 | 0 sec | R&D
26 | ID0026 | Tliq Temp H2 for Fan | >=12 | -30 | 105 | 0 | Yes | 0.5 | 0 sec | R&D
27 | ID0027 | Tliq Temp H3 for Fan | >=22 | -30 | 105 | 0 | Yes | 0.5 | 0 sec | R&D
28 | ID0028 | Tliq Temp H4 for Fan | >=28 | -30 | 105 | 0 | Yes | 0.5 | 0 sec | R&D
29 | ID0029 | Tliq Temp H5 for Fan | >=34 | -30 | 105 | 0 | Yes | 0.5 | 0 sec | R&D
30 | ID0030 | Tliq Temp for Fan | 20 | -30 | 105 | 0 | Yes | 0.5 | 0 sec | R&D
31 | ID0031 | Time of Fan at Lo | 60 sec | 0 | 300 | 0 | Yes | 1 | 0 sec | R&D
32 | ID0032 | ΔT Lo Cool for Auto Fan | 1 | -5 | 5 | 0 | Yes | 1 | 0 sec | R&D
33 | ID0033 | ΔT Me Cool for Auto Fan | 2 | -5 | 5 | 0 | Yes | 1 | 0 sec | R&D
34 | ID0034 | ΔT Hi Cool for Auto Fan | 3 | -5 | 5 | 0 | Yes | 1 | 0 sec | R&D
35 | ID0035 | ΔT Lo Heat for Auto Fan | -1 | -5 | 5 | 0 | Yes | 1 | 0 sec | R&D
36 | ID0036 | ΔT Me Heat for Auto Fan | -2 | -5 | 5 | 0 | Yes | 1 | 0 sec | R&D
37 | ID0037 | ΔT Hi Heat for Auto Fan | -3 | -5 | 5 | 0 | Yes | 1 | 0 sec | R&D
38 | ID0038 | Tliq for DCL 0 | <6 | 0 | 10 | 0 | Yes | 0.5 | 0 sec | R&D
39 | ID0039 | Sleep Mode | 0 | 0-OFF | 1-ON | 0 | Yes | 1 | 0 sec | R&D
40 | ID0040 | Sleep Mode Run Time | 8 hr | 0 | 24 | 0 | Yes | 1 | 0 sec | R&D
41 | ID0041 | Sleep Mode Time C1 | 3 hr | 0 | 24 | 0 | Yes | 1 | 0 sec | R&D
42 | ID0042 | Sleep Mode Time C2 | 2 hr | 0 | 24 | 0 | Yes | 1 | 0 sec | R&D
43 | ID0043 | Sleep Mode Time C3 | 1 hr | 0 | 24 | 0 | Yes | 1 | 0 sec | R&D
44 | ID0044 | Sleep Mode Time C4 | 0 hr | 0 | 24 | 0 | Yes | 1 | 0 sec | R&D
45 | ID0045 | Sleep Mode Set Temp C1 | 16~23 | 0 | 32 | 0 | Yes | 1 | 0 sec | R&D
46 | ID0046 | Sleep Mode Set Temp C2 | 24~27 | 0 | 32 | 0 | Yes | 1 | 0 sec | R&D
47 | ID0047 | Sleep Mode Set Temp C3 | 28~29 | 0 | 32 | 0 | Yes | 1 | 0 sec | R&D
48 | ID0048 | Sleep Mode Set Temp C4 | 30 | 0 | 32 | 0 | Yes | 1 | 0 sec | R&D
49 | ID0049 | Sleep Mode Set Temp H1 | 16 | 0 | 32 | 0 | Yes | 1 | 0 sec | R&D
50 | ID0050 | Sleep Mode Set Temp H2 | 17~23 | 0 | 32 | 0 | Yes | 1 | 0 sec | R&D
51 | ID0051 | Sleep Mode Set Temp H3 | 24~29 | 0 | 32 | 0 | Yes | 1 | 0 sec | R&D
52 | ID0052 | Sleep Mode Set Temp H4 | 30 | 0 | 32 | 0 | Yes | 1 | 0 sec | R&D
53 | ID0053 | Sleep Mode Time H1 | 0 hr | 0 | 24 | 0 | Yes | 1 | 0 sec | R&D
54 | ID0054 | Sleep Mode Time H2 | 1 hr | 0 | 24 | 0 | Yes | 1 | 0 sec | R&D
55 | ID0055 | Sleep Mode Time H3 | 2 hr | 0 | 24 | 0 | Yes | 1 | 0 sec | R&D
56 | ID0056 | Sleep Mode Time H4 | 3 hr | 0 | 24 | 0 | Yes | 1 | 0 sec | R&D
57 | ID0057 | Fan Time at Door Open | 1 min | 0 | 60 | 0 | Yes | 1 | 0 sec | R&D
58 | ID0058 | Fan Speed at Door Open | Lo | 0-OFF | 5-Hi | 0 | Yes | 1 | 0 sec | R&D
59 | ID0059 | EXV Close in IT | -520 | -520 | 480 | 0 | Yes | 1 | 0 sec | R&D
60 | ID0060 | EXV Open in IT | 480 | 0 | 480 | 0 | Yes | 1 | 0 sec | R&D
61 | ID0061 | Flap Position F5 | 90 deg | 0 | 90 | 0 | Yes | 1 | 0 sec | R&D
62 | ID0062 | Flap Position F4 | 72 deg | 0 | 90 | 0 | Yes | 1 | 0 sec | R&D
63 | ID0063 | Flap Position F3 | 54 deg | 0 | 90 | 0 | Yes | 1 | 0 sec | R&D
64 | ID0064 | Flap Position F2 | 36 deg | 0 | 90 | 0 | Yes | 1 | 0 sec | R&D
65 | ID0065 | Flap Position F1 | 18 deg | 0 | 90 | 0 | Yes | 1 | 0 sec | R&D
66 | ID0066 | Flap Position F0 | 0 deg | 0 | 90 | 0 | Yes | 1 | 0 sec | R&D
67 | ID0067 | Flap Time Before Close | 60 sec | 0 | 300 | 0 | Yes | 1 | 0 sec | R&D
68 | ID0068 | Motion Detection | 0 | 0-OFF | 1-ON | 0 | Yes | 1 | 0 sec | R&D
69 | ID0069 | Motion Detection Time | 5 min | 0 | 30 | 0 | Yes | 1 | 0 sec | R&D
70 | ID0070 | Motion Sensor Timer | 30 min | 0 | 60 | 0 | Yes | 1 | 0 sec | R&D
71 | ID0071 | Motion temp A in Cool | 1 | -5 | 5 | 0 | Yes | 1 | 0 sec | R&D
72 | ID0072 | Motion temp A in Heat | -1 | -5 | 5 | 0 | Yes | 1 | 0 sec | R&D
73 | ID0073 | Motion temp B in Cool | 30 | 0 | 32 | 0 | Yes | 1 | 0 sec | R&D
74 | ID0074 | Motion temp B in Heat | 20 | 0 | 32 | 0 | Yes | 1 | 0 sec | R&D
75 | ID0075 | Filter Clean Hrs | 1000 hr | 0 | 10000 | 0 | Yes | 100 | 0 sec | R&D
76 | ID0076 | Filter Clean Fan Time | 30 min | 0 | 100 min | 0 | Yes | 1 | 0 sec | R&D
77 | ID0077 | EXV Open Bypass 1 | 120 | -520 | 480 | 0 | Yes | 1 | 0 sec | R&D
78 | ID0078 | EXV Open Bypass 2 | 150 | -520 | 480 | 0 | Yes | 1 | 0 sec | R&D
79 | ID0079 | EXV Time Bypass 2 | 30 sec | 0 | 100 min | 0 | Yes | 1 | 0 sec | R&D
80 | ID0080 | EXV Interval Bypass 2 | 30 min | 0 | 100 min | 0 | Yes | 1 | 0 sec | R&D
81 | ID0081 | Fan Speed Bypass 2 | OFF | LL | Hi | 0 | Yes | 1 | 0 sec | R&D
82 | ID0082 | Buzzer Time | 500 ms | 100 | 5000 | 0 | Yes | 100 | 0 sec | R&D
83 | ID0083 | Buzzer Time for OFF | 1000 ms | 100 | 5000 | 0 | Yes | 100 | 0 sec | R&D
84 | ID0084 | Hotel Door Key Cool | 27 | 16 | 32 | 0 | Yes | 1 | 0 sec | R&D
85 | ID0085 | Hotel Door Key Heat | 24 | 16 | 32 | 0 | Yes | 1 | 0 sec | R&D
86 | ID0086 | Hotel Door Key Fan | Lo | LL | Hi | 0 | Yes | 1 | 0 sec | R&D
87 | ID0087 | Standby IDU Temp Limit | 20 | 16 | 32 | 0 | Yes | 1 | 0 sec | R&D
88 | ID0088 | TFA & HRV ΔT Cool | -3 | -20 | 0 | 0 | Yes | 1 | 0 sec | R&D
89 | ID0089 | TFA & HRV ΔT Heat | 3 | 20 | 0 | 0 | Yes | 1 | 0 sec | R&D
90 | ID0090 | DI 1 (The digital input selected for DI 1) | Refer module IDU0030 | - | - | 0 | Yes | 1 | 0 sec | R&D
91 | ID0091 | DI 2 (The digital input selected for DI 2) | Refer module IDU0030 | - | - | 0 | Yes | 1 | 0 sec | R&D

## Sheet2-ODU
Sr No | ID number | Set-point | Default | Min | Max | Offset | Need to be stored into EEPROM | Resolution | Time Delay | Authorisation Level
1 | ID0001 | Initial Treatment EXV Close Steps | 3200 | 0 | 6000 | 0 | YES | 1 | 0 | R&D
2 | ID0002 | Superheat Multiplier 1 Method 1 | -0.0000007827 | -10 | 10 | 0 | YES | 1e-11 | 0 | R&D
3 | ID0003 | Superheat Multiplier 2 Method 1 | -0.0010067206 | -10 | 10 | 0 | YES | 1e-11 | 0 | R&D
4 | ID0004 | Superheat Multiplier 3 Method 1 | 0.50476 | -10 | 10 | 0 | YES | 1e-11 | 0 | R&D
5 | ID0005 | Superheat Multiplier 4 Method 1 | -44.4155625726 | -10 | 10 | 0 | YES | 1e-11 | 0 | R&D
6 | ID0006 | Superheat Multiplier For X In Method 2 | 88 | -10 | 200 | 0 | YES | 1 | 0 | R&D
7 | ID0007 | Superheat Multiplier For Y In Method 2 | 14 | -10 | 200 | 0 | YES | 1 | 0 | R&D
8 | ID0008 | Superheat Value Of 103 In Method 2 | 103 | -10 | 200 | 0 | YES | 1 | 0 | R&D
9 | ID0009 | 4 Way Valve Initial State | OFF | ON | OFF | 0 | YES | ON/OFF/Hold Last | 0 | R&D
10 | ID0010 | 4 Way Valve Cool Mode State | OFF | ON | OFF | 0 | YES | ON/OFF/Hold Last | 0 | R&D
11 | ID0011 | 4 Way Valve Heat Mode State | ON | ON | OFF | 0 | YES | ON/OFF/Hold Last | 0 | R&D
12 | ID0012 | 4 Way Valve Off Mode State | Hold last position | ON | OFF | 0 | YES | ON/OFF/Hold Last | 0 | R&D
13 | ID0013 | 4 Way Valve Deforst Mode State | OFF | ON | OFF | 0 | YES | ON/OFF/Hold Last | 0 | R&D
14 | ID0014 | LLSV Cool Mode Run State Time Delay | 0 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
15 | ID0015 | LLSV Cool Mode Stop State Time Delay | 0 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
16 | ID0016 | LLSV Heat Mode Run State Time Delay | 0 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
17 | ID0017 | LLSV Heat Mode Stop State Time Delay | 0 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
18 | ID0018 | Cool Mode Maximum Extra Ratio = 150 % | 150 | 0 | 500 | 0 | YES | 1 | 0 | R&D
19 | ID0019 | Cool Mode Minimum Extra Ratio = 50 % | 50 | 0 | 500 | 0 | YES | 1 | 0 | R&D
20 | ID0020 | Heat Mode Maximum Extra Ratio = 300 % | 300 | 0 | 500 | 0 | YES | 1 | 0 | R&D
21 | ID0021 | Heat Mode Minimum Extra Ratio = 150 % | 150 | 0 | 500 | 0 | YES | 1 | 0 | R&D
22 | ID0022 | TSC In Cool Mode Refrigerant Recovery | 40% | 0 | 100 | 0 | YES | 1 | 0 | R&D
23 | ID0023 | Division Factor For TSC In Normal Operation | 2 | 0 | 10 | 0 | YES | 0.1 | 0 | R&D
24 | ID0024 | Division Factor When TSC < BTC | 20 | 0 | 100 | 0 | YES | 1 | 0 | R&D
25 | ID0025 | Division Factor When TSC > BC | 40 | 0 | 100 | 0 | YES | 1 | 0 | R&D
26 | ID0026 | Multiplication Factor For K In Cool Mode | 1 | -1 | 10 | 0 | YES | 0.1 | 0 | R&D
27 | ID0027 | Multiplication Factor For K In Heat Mode | 1 | -1 | 10 | 0 | YES | 0.1 | 0 | R&D
28 | ID0028 | Multiplication Factor When Thermo ON Capacity Is Changed | 0.3 | -1 | 10 | 0 | YES | 0.1 | 0 | R&D
29 | ID0029 | System 3 Min OFF | 180 sec | 0 | 1800 | 0 | YES | 1 | 0 | R&D
30 | ID0030 | ODU 3 Min OFF | 180 sec | 0 | 1800 | 0 | YES | 1 | 0 | R&D
31 | ID0031 | Inv 3 Min OFF | 180 sec | 0 | 1800 | 0 | YES | 1 | 0 | R&D
32 | ID0032 | 10 Sec Delay | 10 sec | 0 | 100 | 0 | YES | 1 | 0 | R&D
33 | ID0033 | 8 Hours Run Time In Rotation Logic | 480 min | 0 | 4800 | 0 | YES | 1 | 0 | R&D
34 | ID0034 | Step Up 45 % | 45 | 0 | 100 | 0 | YES | 1 | 0 | R&D
35 | ID0035 | Step Up 35% | 35 | 0 | 100 | 0 | YES | 1 | 0 | R&D
36 | ID0036 | Step Up 25% | 25 | 0 | 100 | 0 | YES | 1 | 0 | R&D
37 | ID0037 | ODU Qty Increase 80% | 80 | 0 | 100 | 0 | YES | 1 | 0 | R&D
38 | ID0038 | Step Down 25% | 25 | 0 | 100 | 0 | YES | 1 | 0 | R&D
39 | ID0039 | Step Down 35% | 35 | 0 | 100 | 0 | YES | 1 | 0 | R&D
40 | ID0040 | Step Down 45% | 45 | 0 | 100 | 0 | YES | 1 | 0 | R&D
41 | ID0041 | Tsat HP > 53 | 53 | 0 | 150 | 0 | YES | 1 | 0 | R&D
42 | ID0042 | 9 Min Timer | 9 | 0 | 60 | 0 | YES | 1 | 0 | R&D
43 | ID0043 | Min Tliq < -1 | -1 | -10 | 20 | 0 | YES | 1 | 0 | R&D
44 | ID0044 | 9 Min Timer | 9 | 0 | 60 | 0 | YES | 1 | 0 | R&D
45 | ID0045 | DLT Limit 1 | 110 | 0 | 150 | 0 | YES | 1 | 0 | R&D
46 | ID0046 | DLT Limit 2 | 100 | 0 | 150 | 0 | YES | 1 | 0 | R&D
47 | ID0047 | DLT Limit 3 | 96 | 0 | 150 | 0 | YES | 1 | 0 | R&D
48 | ID0048 | DLT Limit 4 | 93 | 0 | 150 | 0 | YES | 1 | 0 | R&D
49 | ID0049 | IDU IR 80% | 80 | 0 | 300 | 0 | YES | 1 | 0 | R&D
50 | ID0050 | IDU Down Rate 0.4 Kw | 0.4 | 0 | 5 | 0 | YES | 0.1 | 0 | R&D
51 | ID0051 | LPS Limit 1 | 55 | 0 | 400 | 0 | YES | 1 | 0 | R&D
52 | ID0052 | LPS Limit 2 | 39 | 0 | 400 | 0 | YES | 1 | 0 | R&D
53 | ID0053 | LPS Limit 3 | 34 | 0 | 400 | 0 | YES | 1 | 0 | R&D
54 | ID0054 | LPS Limit 4 | 29 | 0 | 400 | 0 | YES | 1 | 0 | R&D
55 | ID0055 | LPS Down Rate | 1 | 0 | 5 | 0 | YES | 0.1 | 0 | R&D
56 | ID0056 | Cool HPS Limit 1 | 600 | 0 | 800 | 0 | YES | 1 | 0 | R&D
57 | ID0057 | Cool HPS Limit 2 | 585 | 0 | 800 | 0 | YES | 1 | 0 | R&D
58 | ID0058 | Cool HPS Limit 3 | 570 | 0 | 800 | 0 | YES | 1 | 0 | R&D
59 | ID0059 | Cool HPS Down Rate | 1.2 | 0 | 800 | 0 | YES | 1 | 0 | R&D
60 | ID0060 | Heat HPS Limit 1 | 579 | 0 | 800 | 0 | YES | 1 | 0 | R&D
61 | ID0061 | Heat HPS Limit 2 | 518 | 0 | 800 | 0 | YES | 1 | 0 | R&D
62 | ID0062 | Heat HPS Limit 3 | 484 | 0 | 800 | 0 | YES | 1 | 0 | R&D
63 | ID0063 | Heat HPS Limit 4 | 462 | 0 | 800 | 0 | YES | 1 | 0 | R&D
64 | ID0064 | Heat HPS Limit 5 | 420 | 0 | 800 | 0 | YES | 1 | 0 | R&D
65 | ID0065 | Heat HPS Down Rate 1 | 4 | 0 | 10 | 0 | YES | 0.1 | 0 | R&D
66 | ID0066 | Heat HPS Down Rate 2 | 2 | 0 | 10 | 0 | YES | 0.1 | 0 | R&D
67 | ID0067 | Heat HPS Down Rate 3 | 0.4 | 0 | 5 | 0 | YES | 0.1 | 0 | R&D
68 | ID0068 | HP Switch Trip Count | 3 | 0 | 10 | 0 | YES | 1 | 0 | R&D
69 | ID0069 | HP Switch Trip Time | 60 min | 0 | 600 | 0 | YES | 1 | 0 | R&D
70 | ID0070 | Frozen Initial Down Bypasss | 3 min | 1 | 60 | 0 | YES | 1 | 0 | R&D
71 | ID0071 | Frozen Limit 1 | 6 Deg | -10 | 20 | 0 | YES | 0.5 | 0 | R&D
72 | ID0072 | Frozen Limit 2 | -2 Deg | -20 | 20 | 0 | YES | 0.5 | 0 | R&D
73 | ID0073 | Frozen Down Rate | 0.4 KW | 0 | 10 | 0 | YES | 0.1 | 0 | R&D
74 | ID0074 | Delta P Limit 1 | 1 | 0 | 5 | 0 | YES | 0.1 | 0 | R&D
75 | ID0075 | Delta P Limit 2 | 0.5 | 0 | 5 | 0 | YES | 0.1 | 0 | R&D
76 | ID0076 | Delta P Limit 3 | 0.4 | 0 | 5 | 0 | YES | 0.1 | 0 | R&D
77 | ID0077 | Delta P Increase Rate 1 | 0.2 | 0 | 5 | 0 | YES | 0.1 | 0 | R&D
78 | ID0078 | Delat P Increase Rate 2 | 0.4 | 0 | 5 | 0 | YES | 0.1 | 0 | R&D
79 | ID0079 | IPM Limit 1 | 100 | 0 | 200 | 0 | YES | 1 | 0 | R&D
80 | ID0080 | IPM Limit 2 | 93 | 0 | 200 | 0 | YES | 1 | 0 | R&D
81 | ID0081 | IPM Limit 3 | 87 | 0 | 200 | 0 | YES | 1 | 0 | R&D
82 | ID0082 | IPM Limit 4 | 85 | 0 | 200 | 0 | YES | 1 | 0 | R&D
83 | ID0083 | IPM Down Rate | 1 | 0 | 200 | 0 | YES | 1 | 0 | R&D
84 | ID0084 | IPM IR | 60 | 0 | 200 | 0 | YES | 1 | 0 | R&D
85 | ID0085 | Ascending amb limit | 48 | 0 | 70 | 0 | YES | 1 | 0 | R&D
86 | ID0086 | RPS limit | 75 | 0 | 120 | 0 | YES | 1 | 0 | R&D
87 | ID0087 | Descending amb limit | 45 | 0 | 70 | 0 | YES | 1 | 0 | R&D
88 | ID0088 | Start up control time | 60 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
89 | ID0089 | 4WV in ① (OFF ) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
90 | ID0090 | ULV1 in ① (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
91 | ID0091 | ULV2 in ① (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
92 | ID0092 | SV1 in ① (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
93 | ID0093 | SV2 in ① (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
94 | ID0094 | SV3 in ① (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
95 | ID0095 | EXV(o) in ① | ※1 | ※1 | ※3 | 0 | YES | ※1 | 0 | R&D
96 | ID0096 | EXV(i) in ① | 0 | 0 | 3000 | 0 | YES | 1 | 0 | R&D
97 | ID0097 | Fan(o) in ① (Normal) [ User will either select "Normal operation" or fan control factor ] | Normal Control | 0 | 19 | 0 | YES | 1/NC | 0 | R&D
98 | ID0098 | Fan(i) in ① (Normal)[User will be able to select "Normal operation , OFF, Low low , low , mid , high ] | Normal Control | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low , low , mid , high | 0 | R&D
99 | ID0099 | "A" condition in ① Min | 20 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
100 | ID0100 | "A" condition in ① Max | 60 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
101 | ID0101 | "B" condition in ① | OPEN | OPEN | CLOSE | 0 | YES | Open/Close | 0 | R&D
102 | ID0102 | "C" condition in ① | 100 psi | 0 | 150 | 0 | YES | 1 | 0 | R&D
103 | ID0103 | "D" condition in ① (True) [ User should be able to select a custom logic part that he might have written ] | TRUE | TRUE | FALSE | 0 | YES | True/False | 0 | R&D
104 | ID0104 | "E" condition in ① (True) [ User should be able to select a custom logic part that he might have written ] | TRUE | TRUE | FALSE | 0 | YES | True/False | 0 | R&D
105 | ID0105 | "F" condition in ① (True) [ User should be able to select a custom logic part that he might have written ] | TRUE | TRUE | FALSE | 0 | YES | True/False | 0 | R&D
106 | ID0106 | 4WV in ② (OFF ) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
107 | ID0107 | ULV1 in ② (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
108 | ID0108 | ULV2 in ② (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
109 | ID0109 | SV1 in ② (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
110 | ID0110 | SV2 in ② (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
111 | ID0111 | SV3 in ② (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
112 | ID0112 | EXV(o) in ② | ※1 | ※1 | ※3 | 0 | YES | ※1 | 0 | R&D
113 | ID0113 | EXV(i) in ② [ user will either select "as per flow chart" or value ] | 0 | 0 | 3000 | 0 | YES | 1 | 0 | R&D
114 | ID0114 | Fan(o) in ② (Normal) [ User will either select "Normal operation" or fan control factor ] | Normal Control | 0 | 19 | 0 | YES | 1/NC | 0 | R&D
115 | ID0115 | Fan(i) in ② (Normal)[User will be able to select "Normal operation , OFF, Low low , low , mid , high ] | Normal Control | low low | high | 0 | YES | NC/OFF, Low low , low , mid , high | 0 | R&D
116 | ID0116 | "A" condition in ② Min | 10 | 0 | 600 | 0 | YES | 1 | 0 | R&D
117 | ID0117 | "A" condition in ② Max | 60 | 0 | 600 | 0 | YES | 1 | 0 | R&D
118 | ID0118 | "B" condition in ② | Open | Close | Open | 0 | YES | Open/Close | 0 | R&D
119 | ID0119 | "C" condition in ② | 100 | 0 | 600 | 0 | YES | 1 | 0 | R&D
120 | ID0120 | "D" condition in ② (Default) [ User should be able to select a default ( DSH>10) or custom logic part that he might have written ] | Default | TRUE | FALSE | 0 | YES | True/False | 0 | R&D
121 | ID0121 | "D" condition value in ② | 10 | 0 | 50 | 0 | YES | 1 | 0 | R&D
122 | ID0122 | "E" condition in ② (True) [ User should be able to select a custom logic part that he might have written ] | TRUE | TRUE | FALSE | 0 | YES | True/False | 0 | R&D
123 | ID0123 | "F" condition in ② (True) [ User should be able to select a custom logic part that he might have written ] | TRUE | TRUE | FALSE | 0 | YES | True/False | 0 | R&D
124 | ID0124 | 4WV in ⑤ (OFF ) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
125 | ID0125 | ULV1 in ⑤ (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
126 | ID0126 | ULV2 in ⑤ (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
127 | ID0127 | SV1 in ⑤ (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
128 | ID0128 | SV2 in ⑤ (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
129 | ID0129 | SV3 in ⑤ (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
130 | ID0130 | EXV(o) in ⑤ | ※1 | ※1 | ※3 | 0 | YES | ※1 | 0 | R&D
131 | ID0131 | EXV(i) in ⑤ (As per flow chart)[ user will either select "as per flow chart" or value ] | as per flow chart | 0 | 3000 | 0 | YES | 1 | 0 | R&D
132 | ID0132 | Fan(o) in ⑤ (Normal) [ User will either select "Normal operation" or fan control factor ] | Normal Control | 0 | 19 | 0 | YES | 1/NC | 0 | R&D
133 | ID0133 | Fan(i) in ⑤ (Normal)[User will be able to select "Normal operation , OFF, Low low , low , mid , high ] | Normal Control | low low | high | 0 | YES | NC/OFF, Low low , low , mid , high | 0 | R&D
134 | ID0134 | "A" condition in ⑤ | 180 | 0 | 600 | 0 | YES | 1 | 0 | R&D
135 | ID0135 | "B" condition in ⑤ | Open | Close | Open | 0 | YES | Open/Close | 0 | R&D
136 | ID0136 | "C" condition in ⑤ | 100 | 0 | 600 | 0 | YES | 1 | 0 | R&D
137 | ID0137 | "D" condition in ⑤ (True) [ User should be able to select a custom logic part that he might have written ] | TRUE | TRUE | FALSE | 0 | YES | True/False | 0 | R&D
138 | ID0138 | "E" condition in ⑤ (True) [ User should be able to select a custom logic part that he might have written ] | TRUE | TRUE | FALSE | 0 | YES | True/False | 0 | R&D
139 | ID0139 | "F" condition in ⑤ (True) [ User should be able to select a custom logic part that he might have written ] | TRUE | TRUE | FALSE | 0 | YES | True/False | 0 | R&D
140 | ID0140 | 4WV in ③ (ON ) [ User should also be able to select NA ] | ON | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
141 | ID0141 | ULV1 in ③ (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
142 | ID0142 | ULV2 in ③ (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
143 | ID0143 | SV1 in ③ (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
144 | ID0144 | SV2 in ③ (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
145 | ID0145 | SV3 in ③ (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
146 | ID0146 | EXV(o) in ③ | ※2 | ※1 | ※3 | 0 | YES | ※1 | 0 | R&D
147 | ID0147 | EXV(i) in ③ (As per flow chart)[ user will either select "as per flow chart" or value ] | 480 | 1 | 3000 | 0 | YES | 1 | 0 | R&D
148 | ID0148 | Fan(o) in ③ (Normal) [ User will either select "Normal operation" or fan control factor ] | Normal Control | 0 | 19 | 0 | YES | 1/NC | 0 | R&D
149 | ID0149 | Fan(i) in ③ (Normal)[User will be able to select "Normal operation , OFF, Low low , low , mid , high ] | Normal Control | low low | high | 0 | YES | NC/OFF, Low low , low , mid , high | 0 | R&D
150 | ID0150 | "A" condition in ③ Min | 20 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
151 | ID0151 | "A" condition in ③ Max | 60 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
152 | ID0152 | "B" condition in ③ | 420 | 0 | 700 | 0 | YES | 1 | 0 | R&D
153 | ID0153 | "C" condition in ③ (True)[ User should be able to select a custom logic part that he might have written ] | TRUE | TRUE | FALSE | 0 | YES | True/False | 0 | R&D
154 | ID0154 | "D" condition in ③ (True) [ User should be able to select a custom logic part that he might have written ] | TRUE | TRUE | FALSE | 0 | YES | True/False | 0 | R&D
155 | ID0155 | "E" condition in ③ (True) [ User should be able to select a custom logic part that he might have written ] | TRUE | TRUE | FALSE | 0 | YES | True/False | 0 | R&D
156 | ID0156 | "F" condition in ③ (True)[ User should be able to select a custom logic part that he might have written ] | TRUE | TRUE | FALSE | 0 | YES | True/False | 0 | R&D
157 | ID0157 | 4WV in ④ (ON ) [ User should also be able to select NA ] | ON | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
158 | ID0158 | ULV1 in ④ (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
159 | ID0159 | ULV2 in ④ (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
160 | ID0160 | SV1 in ④ (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
161 | ID0161 | SV2 in ④ (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
162 | ID0162 | SV3 in ④ (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
163 | ID0163 | EXV(o) in ④ | ※3 | ※1 | ※3 | 0 | YES | ※1 | 0 | R&D
164 | ID0164 | EXV(i) in ④ (480)[ user will either select "as per flow chart" or value ] | 480 | 0 | 3000 | 0 | YES | 1 | 0 | R&D
165 | ID0165 | Fan(o) in ④ (Normal) [ User will either select "Normal operation" or fan control factor ] | Normal Control | 0 | 19 | 0 | YES | 1/NC | 0 | R&D
166 | ID0166 | Fan(i) in ④ (Normal)[User will be able to select "Normal operation , OFF, Low low , low , mid , high ] | Normal Control | low low | high | 0 | YES | NC/OFF, Low low , low , mid , high | 0 | R&D
167 | ID0167 | "A" condition in ④ | 10min | 0 | 180 min | 0 | YES | 1 | 0 | R&D
168 | ID0168 | "B" condition min Tliq in ④ | 30 | -10 | 90 | 0 | YES | 1 | 0 | R&D
169 | ID0169 | "B" condition T_Sat HP in ④ | 462 | 0 | 700 | 0 | YES | 1 | 0 | R&D
170 | ID0170 | "C" condition in ④ | TRUE | FALSE | TRUE | 0 | YES | True/False | 0 | R&D
171 | ID0171 | "D" condition in ④ (10) [ User should be able to select a custom logic part that he might have written ] | 10 | 0 | 50 | 0 | YES | 1 | 0 | R&D
172 | ID0172 | "E" condition in ④ | TRUE | FALSE | TRUE | 0 | YES | True/False | 0 | R&D
173 | ID0173 | "F" condition in ④ | TRUE | FALSE | TRUE | 0 | YES | True/False | 0 | R&D
174 | ID0174 | 4WV in ⑥ (ON ) [ User should also be able to select NA ] | ON | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
175 | ID0175 | ULV1 in ⑥ (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
176 | ID0176 | ULV2 in ⑥ (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
177 | ID0177 | SV1 in ⑥ (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
178 | ID0178 | SV2 in ⑥ (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
179 | ID0179 | SV3 in ⑥ (OFF) [ User should also be able to select NA ] | OFF | OFF | ON | 0 | YES | ON/OFF/NA | 0 | R&D
180 | ID0180 | EXV(o) in ⑥ | ※3 | ※1 | ※3 | 0 | YES | ※1 | 0 | R&D
181 | ID0181 | EXV(i) in ⑥ (As per flow chart)[ user will either select "as per flow chart" or value ] | as per flow chart | 0 | 3000 | 0 | YES | 1 | 0 | R&D
182 | ID0182 | Fan(o) in ⑥ (Normal) [ User will either select "Normal operation" or fan control factor ] | Normal Control | 0 | 19 | 0 | YES | 1/NC | 0 | R&D
183 | ID0183 | Fan(i) in ⑥ (Normal)[User will be able to select "Normal operation , OFF, Low low , low , mid , high ] | Normal Control | low low | high | 0 | YES | NC/OFF, Low low , low , mid , high | 0 | R&D
184 | ID0184 | "A" condition in ⑥ | 180 | 0 | 600 | 0 | YES | 1 | 0 | R&D
185 | ID0185 | "B" condition in ⑥ | TRUE | FALSE | TRUE | 0 | YES | True/False | 0 | R&D
186 | ID0186 | "C" condition in ⑥ | TRUE | FALSE | TRUE | 0 | YES | True/False | 0 | R&D
187 | ID0187 | "D" condition in ⑥ (True) [ User should be able to select a custom logic part that he might have written ] | TRUE | FALSE | TRUE | 0 | YES | True/False | 0 | R&D
188 | ID0188 | "E" condition in ⑥ | TRUE | FALSE | TRUE | 0 | YES | True/False | 0 | R&D
189 | ID0189 | "F" condition in ⑥ | TRUE | FALSE | TRUE | 0 | YES | True/False | 0 | R&D
190 | ID0190 | ※1 in A | 3000 | 0 | 3000 | 0 | YES | 1 | 0 | R&D
191 | ID0191 | ※1 in B | 3000 | 0 | 3000 | 0 | YES | 1 | 0 | R&D
192 | ID0192 | ※2 in A | 850 | 0 | 3000 | 0 | YES | 1 | 0 | R&D
193 | ID0193 | ※2 in B | 600 | 0 | 3000 | 0 | YES | 1 | 0 | R&D
194 | ID0194 | ※3 in A | 1000 | 0 | 3000 | 0 | YES | 1 | 0 | R&D
195 | ID0195 | ※3 in B | 1000 | 0 | 3000 | 0 | YES | 1 | 0 | R&D
196 | ID0196 | 2 Fan sys step 1 | (0,250) | (0,0) | (1200,1200) | 0 | YES | 5,5 | 0 | R&D
197 | ID0197 | 2 Fan sys step 2 | (0,325) | (0,0) | (1200,1200) | 0 | YES | 5,5 | 0 | R&D
198 | ID0198 | 2 Fan sys step 3 | (0,400) | (0,0) | (1200,1200) | 0 | YES | 5,5 | 0 | R&D
199 | ID0199 | 2 Fan sys step 4 | (0,475) | (0,0) | (1200,1200) | 0 | YES | 5,5 | 0 | R&D
200 | ID0200 | 2 Fan sys step 5 | (0,550) | (0,0) | (1200,1200) | 0 | YES | 5,5 | 0 | R&D
201 | ID0201 | 2 Fan sys step 6 | (0,650) | (0,0) | (1200,1200) | 0 | YES | 5,5 | 0 | R&D
202 | ID0202 | 2 Fan sys step 7 | (250,250) | (0,0) | (1200,1200) | 0 | YES | 5,5 | 0 | R&D
203 | ID0203 | 2 Fan sys step 8 | (325,325) | (0,0) | (1200,1200) | 0 | YES | 5,5 | 0 | R&D
204 | ID0204 | 2 Fan sys step 9 | (400,400) | (0,0) | (1200,1200) | 0 | YES | 5,5 | 0 | R&D
205 | ID0205 | 2 Fan sys step 10 | (475,475) | (0,0) | (1200,1200) | 0 | YES | 5,5 | 0 | R&D
206 | ID0206 | 2 Fan sys step 11 | (550,550) | (0,0) | (1200,1200) | 0 | YES | 5,5 | 0 | R&D
207 | ID0207 | 2 Fan sys step 12 | (625,625) | (0,0) | (1200,1200) | 0 | YES | 5,5 | 0 | R&D
208 | ID0208 | 2 Fan sys step 13 | (700,700) | (0,0) | (1200,1200) | 0 | YES | 5,5 | 0 | R&D
209 | ID0209 | 2 Fan sys step 14 | (775,775) | (0,0) | (1200,1200) | 0 | YES | 5,5 | 0 | R&D
210 | ID0210 | 2 Fan sys step 15 | (850,850) | (0,0) | (1200,1200) | 0 | YES | 5,5 | 0 | R&D
211 | ID0211 | 2 Fan sys step 16 | (925,925) | (0,0) | (1200,1200) | 0 | YES | 5,5 | 0 | R&D
212 | ID0212 | 2 Fan sys step 17 | (1000,1000) | (0,0) | (1200,1200) | 0 | YES | 5,5 | 0 | R&D
213 | ID0213 | 2 Fan sys step 18 | (1075,1075) | (0,0) | (1200,1200) | 0 | YES | 5,5 | 0 | R&D
214 | ID0214 | 2 Fan sys step 19 | (1150,1150) | (0,0) | (1200,1200) | 0 | YES | 5,5 | 0 | R&D
215 | ID0215 | 2 Fan sys step 20 | (1200,1200) | (0,0) | (1200,1200) | 0 | YES | 5,5 | 0 | R&D
216 | ID0216 | 1 Fan sys step 1 | (200) | (0) | (1200) | 0 | YES | 5 | 0 | R&D
217 | ID0217 | 1 Fan sys step 2 | (300) | (0) | (1200) | 0 | YES | 5 | 0 | R&D
218 | ID0218 | 1 Fan sys step 3 | (350) | (0) | (1200) | 0 | YES | 5 | 0 | R&D
219 | ID0219 | 1 Fan sys step 4 | (400) | (0) | (1200) | 0 | YES | 5 | 0 | R&D
220 | ID0220 | 1 Fan sys step 5 | (450) | (0) | (1200) | 0 | YES | 5 | 0 | R&D
221 | ID0221 | 1 Fan sys step 6 | (500) | (0) | (1200) | 0 | YES | 5 | 0 | R&D
222 | ID0222 | 1 Fan sys step 7 | (550) | (0) | (1200) | 0 | YES | 5 | 0 | R&D
223 | ID0223 | 1 Fan sys step 8 | (600) | (0) | (1200) | 0 | YES | 5 | 0 | R&D
224 | ID0224 | 1 Fan sys step 9 | (650) | (0) | (1200) | 0 | YES | 5 | 0 | R&D
225 | ID0225 | 1 Fan sys step 10 | (700) | (0) | (1200) | 0 | YES | 5 | 0 | R&D
226 | ID0226 | 1 Fan sys step 11 | (750) | (0) | (1200) | 0 | YES | 5 | 0 | R&D
227 | ID0227 | 1 Fan sys step 12 | (800) | (0) | (1200) | 0 | YES | 5 | 0 | R&D
228 | ID0228 | 1 Fan sys step 13 | (850) | (0) | (1200) | 0 | YES | 5 | 0 | R&D
229 | ID0229 | 1 Fan sys step 14 | (900) | (0) | (1200) | 0 | YES | 5 | 0 | R&D
230 | ID0230 | 1 Fan sys step 15 | (950) | (0) | (1200) | 0 | YES | 5 | 0 | R&D
231 | ID0231 | 1 Fan sys step 16 | (1000) | (0) | (1200) | 0 | YES | 5 | 0 | R&D
232 | ID0232 | 1 Fan sys step 17 | (1050) | (0) | (1200) | 0 | YES | 5 | 0 | R&D
233 | ID0233 | 1 Fan sys step 18 | (1100) | (0) | (1200) | 0 | YES | 5 | 0 | R&D
234 | ID0234 | 1 Fan sys step 19 | (1200) | (0) | (1200) | 0 | YES | 5 | 0 | R&D
235 | ID0235 | Fan Ambient temp upper limit (35) | 35 | 0 | 60 | 0 | YES | 1 | 0 | R&D
236 | ID0236 | Fan Ambient temp lower limit (15) | 15 | 0 | 60 | 0 | YES | 1 | 0 | R&D
237 | ID0237 | Fan amb high Cfactor (10) | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
238 | ID0238 | Fan amb mid Cfactor (8) | 8 | 0 | 19 | 0 | YES | 1 | 0 | R&D
239 | ID0239 | Fan amb low Cfactor (6) | 6 | 0 | 19 | 0 | YES | 1 | 0 | R&D
240 | ID0240 | Fan HP limit 1 (541) | 541 | 0 | 900 | 0 | YES | 1 | 0 | R&D
241 | ID0241 | Fan HP limit 2 (381) | 381 | 0 | 900 | 0 | YES | 1 | 0 | R&D
242 | ID0242 | Fan HP limit 3 (345) | 345 | 0 | 900 | 0 | YES | 1 | 0 | R&D
243 | ID0243 | Fan HP max step (19) | 19 | 0 | 19 | 0 | YES | 1 | 0 | R&D
244 | ID0244 | Fan HP Cfactor up (2) | 2 | -2 | 10 | 0 | YES | 1 | 0 | R&D
245 | ID0245 | Fan HP Cfactor down (2) | 2 | -2 | 10 | 0 | YES | 1 | 0 | R&D
246 | ID0246 | Fan off run time (30) | 30 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
247 | ID0247 | Heat mode 1 min interval (1) | 1 min | 0 | 10 | 0 | YES | 1 | 0 | R&D
248 | ID0248 | Heat mode fan speed up step (1) | 1 | 0 | 19 | 0 | YES | 1 | 0 | R&D
249 | ID0249 | Heat mode fan speed up time (1) | 1 min | 0 | 10 | 0 | YES | 1 | 0 | R&D
250 | ID0250 | Heat mode fan up High perssure (53) | 53 psi | 0 | 600 | 0 | YES | 1 | 0 | R&D
251 | ID0251 | Heat mode fan speed down step (2) | 2 | 0 | 19 | 0 | YES | 1 | 0 | R&D
252 | ID0252 | Heat mode fan speed down time (1) | 1 | 0 | 10 | 0 | YES | 1 | 0 | R&D
253 | ID0253 | Heat mode amb temp for initial set high lim (20) | 20 | 0 | 50 | 0 | YES | 1 | 0 | R&D
254 | ID0254 | Heat mode amb temp for initial set low lim (20) | 10 | 0 | 50 | 0 | YES | 1 | 0 | R&D
255 | ID0255 | Heat mode Fan high initial set ( 6 ) | 6 | 0 | 19 | 0 | YES | 1 | 0 | R&D
256 | ID0256 | Heat mode Fan mid initial set ( 6 ) | 8 | 0 | 19 | 0 | YES | 1 | 0 | R&D
257 | ID0257 | Heat mode Fan low initial set ( 6 ) | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
258 | ID0258 | Condensor clean time limit 1 (20) | 20 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
259 | ID0259 | Condensor clean time limit 2 (130) | 130 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
260 | ID0260 | Condensor clean time limit 3 (150) | 150 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
261 | ID0261 | IEC IDU switch off EXV step (16) | 16 | 0 | 480 | 0 | YES | 1 | 0 | R&D
262 | ID0262 | IEC IDU Thermo oFF exv step (3) | 3 | 0 | 480 | 0 | YES | 1 | 0 | R&D
263 | ID0263 | IEC SHtgt (2) | 2 | -5 | 10 | 0 | YES | 1 | 0 | R&D
264 | ID0264 | IEC ΔT_tgt lower limit (1) | 1 | -5 | 10 | 0 | YES | 1 | 0 | R&D
265 | ID0265 | IEC ΔT ≦ 0 (0) | 0 | -5 | 10 | 0 | YES | 1 | 0 | R&D
266 | ID0266 | IEC add (3) | 3 | 0 | 10 | 0 | YES | 1 | 0 | R&D
267 | ID0267 | IEC floodback detection ΔT ≦ 0 deg (0) | 0 | -5 | 20 | 0 | YES | 1 | 0 | R&D
268 | ID0268 | IEC ΔEXV=-2 (-2) | -2 | -5 | 10 | 0 | YES | 1 | 0 | R&D
269 | ID0269 | IEC dlt limit Max(DLT)≧ 104 (104) | 104 | 0 | 150 | 0 | YES | 1 | 0 | R&D
270 | ID0270 | IEC floodback multi Counter*0.5 (0.5) | 0.5 | 0 | 10 | 0 | YES | 0.5 | 0 | R&D
271 | ID0271 | IEC floodback counter (7) | 7 | 0 | 20 | 0 | YES | 1 | 0 | R&D
272 | ID0272 | IEC EXV≦ 45 (45) | 45 | 0 | 480 | 0 | YES | 1 | 0 | R&D
273 | ID0273 | IEH IDU switch off EXV step (16) | 16 | 0 | 480 | 0 | YES | 1 | 0 | R&D
274 | ID0274 | IEH IDU ΔT≦ 2 deg | 2 | 0 | 10 | 0 | YES | 1 | 0 | R&D
275 | ID0275 | IEH Counter 4 (4) | 4 | 0 | 10 | 0 | YES | 1 | 0 | R&D
276 | ID0276 | OEH ΔECC (30) | 30 | 0 | 50 | 0 | YES | 1 | 0 | R&D
277 | ID0277 | OEH Sh_Tgt value ( 2) | 2 | 0 | 10 | 0 | YES | 1 | 0 | R&D
278 | ID0278 | OEH delta T lower target (0) | 0 | 0 | 10 | 0 | YES | 1 | 0 | R&D
279 | ID0279 | Defrost comp on timer (25 min) | 25 min | 0 | 60 | 0 | YES | 1 | 0 | R&D
280 | ID0280 | Defrost 4 min timer ( 4 min ) | 4 min | 0 | 30 | 0 | YES | 1 | 0 | R&D
281 | ID0281 | Defrost counter times (2 ) | 2 | 0 | 5 | 0 | YES | 1 | 0 | R&D
282 | ID0282 | Defrost table B0 (80) | 80 | 0 | 600 | 0 | YES | 1 | 0 | R&D
283 | ID0283 | Defrost table C0 (12) | 12 | 0 | 30 | 0 | YES | 1 | 0 | R&D
284 | ID0284 | Defrost table D0 (80) | 80 | 0 | 600 | 0 | YES | 1 | 0 | R&D
285 | ID0285 | Defrost table C1 (ON) | ON | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
286 | ID0286 | Defrost table F1 (OFF) | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
287 | ID0287 | Defrost table B2 (min) | Min | 0 | 90 | 0 | YES | 1 | 0 | R&D
288 | ID0288 | Defrost table C2 (80) | 80 | 0 | 600 | 0 | YES | 1 | 0 | R&D
289 | ID0289 | Defrost table D2 (0) | 0 | 0 | 90 | 0 | YES | 1 | 0 | R&D
290 | ID0290 | Defrost table B3 (13) | 13 | 0 | 19 | 0 | YES | 1 | 0 | R&D
291 | ID0291 | Defrost table C3 (Stop) | Stop | 0 | 19 | 0 | YES | 1 | 0 | R&D
292 | ID0292 | Defrost table D3 (13) | 13 | 0 | 19 | 0 | YES | 1 | 0 | R&D
293 | ID0293 | Defrost table B4 (600) | 600 | 0 | 3000 | 0 | YES | 1 | 0 | R&D
294 | ID0294 | Defrost table C4 (3000) | 3000 | 0 | 3000 | 0 | YES | 1 | 0 | R&D
295 | ID0295 | Defrost table B6 (ON) | ON | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
296 | ID0296 | Defrost table C6 (OFF) | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
297 | ID0297 | Defrost table B7 (OFF) | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
298 | ID0298 | Defrost table C7 (ON) | ON | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
299 | ID0299 | Defrost table F7 (OFF) | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
300 | ID0300 | Defrost table C8 (ON) | ON | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
301 | ID0301 | Defrost table F8 (120) | 120 | 0 | 600 | 0 | YES | 1 | 0 | R&D
302 | ID0302 | Defrost table C10 (100) | 100 | 0 | 480 | 0 | YES | 1 | 0 | R&D
303 | ID0303 | Defrost table D10 (100) | 100 | 0 | 480 | 0 | YES | 1 | 0 | R&D
304 | ID0304 | Defrost table B11 (Min) | Min | 0 | 19 | 0 | YES | 1 | 0 | R&D
305 | ID0305 | Defrost table C11 ( Stop ) | Stop | 0 | 19 | 0 | YES | 1 | 0 | R&D
306 | ID0306 | Defrost table F11 (120) | 120 | 0 | 600 | 0 | YES | 1 | 0 | R&D
307 | ID0307 | Defrost table C12 (100) | 100 | 0 | 480 | 0 | YES | 1 | 0 | R&D
308 | ID0308 | Defrost table F12 | 0 | 0 | 480 | 0 | YES | 1 | 0 | R&D
309 | ID0309 | Defrost table C14 (100) | 100 | 0 | 480 | 0 | YES | 1 | 0 | R&D
310 | ID0310 | Defrost table D14 (100) | 100 | 0 | 480 | 0 | YES | 1 | 0 | R&D
311 | ID0311 | Defrost table C15 (OFF) | OFF | 0 | 19 | 0 | YES | 1 | 0 | R&D
312 | ID0312 | Defrost table F15 (OFF) | OFF | 0 | 19 | 0 | YES | 1 | 0 | R&D
313 | ID0313 | Defrost table C16 (100) | 100 | 0 | 480 | 0 | YES | 1 | 0 | R&D
314 | ID0314 | Defrost table F16 (OFF) | OFF | 0 | 480 | 0 | YES | 1 | 0 | R&D
315 | ID0315 | ODC-A1 | 11.33 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
316 | ID0316 | ODC-A2 | 11.78 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
317 | ID0317 | ODC-A3 | 12.23 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
318 | ID0318 | ODC-A4 | 12.68 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
319 | ID0319 | ODC-A5 | 13.13 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
320 | ID0320 | ODC-A6 | 13.58 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
321 | ID0321 | ODC-A7 | 14 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
322 | ID0322 | ODC-A8 | 14.125 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
323 | ID0323 | ODC-A9 | 14.25 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
324 | ID0324 | ODC-A10 | 14.375 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
325 | ID0325 | ODC-A11 | 14.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
326 | ID0326 | ODC-A12 | 14.625 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
327 | ID0327 | ODC-A13 | 14.75 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
328 | ID0328 | ODC-A14 | 14.875 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
329 | ID0329 | ODC-A15 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
330 | ID0330 | ODC-A16 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
331 | ID0331 | ODC-A17 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
332 | ID0332 | ODC-B1 | 11.8967 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
333 | ID0333 | ODC-B2 | 12.2467 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
334 | ID0334 | ODC-B3 | 12.5967 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
335 | ID0335 | ODC-B4 | 12.9467 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
336 | ID0336 | ODC-B5 | 13.2967 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
337 | ID0337 | ODC-B6 | 13.6467 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
338 | ID0338 | ODC-B7 | 14 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
339 | ID0339 | ODC-B8 | 14.125 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
340 | ID0340 | ODC-B9 | 14.25 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
341 | ID0341 | ODC-B10 | 14.375 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
342 | ID0342 | ODC-B11 | 14.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
343 | ID0343 | ODC-B12 | 14.625 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
344 | ID0344 | ODC-B13 | 14.75 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
345 | ID0345 | ODC-B14 | 14.875 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
346 | ID0346 | ODC-B15 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
347 | ID0347 | ODC-B16 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
348 | ID0348 | ODC-B17 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
349 | ID0349 | ODC-C1 | 12.4633 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
350 | ID0350 | ODC-C2 | 12.88 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
351 | ID0351 | ODC-C3 | 13.2967 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
352 | ID0352 | ODC-C4 | 13.7133 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
353 | ID0353 | ODC-C5 | 14.13 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
354 | ID0354 | ODC-C6 | 14.5467 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
355 | ID0355 | ODC-C7 | 14 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
356 | ID0356 | ODC-C8 | 14.125 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
357 | ID0357 | ODC-C9 | 14.25 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
358 | ID0358 | ODC-C10 | 14.375 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
359 | ID0359 | ODC-C11 | 14.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
360 | ID0360 | ODC-C12 | 14.625 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
361 | ID0361 | ODC-C13 | 14.75 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
362 | ID0362 | ODC-C14 | 14.875 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
363 | ID0363 | ODC-C15 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
364 | ID0364 | ODC-C16 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
365 | ID0365 | ODC-C17 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
366 | ID0366 | ODC-D1 | 13 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
367 | ID0367 | ODC-D2 | 13.1667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
368 | ID0368 | ODC-D3 | 13.3333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
369 | ID0369 | ODC-D4 | 13.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
370 | ID0370 | ODC-D5 | 13.6667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
371 | ID0371 | ODC-D6 | 13.8333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
372 | ID0372 | ODC-D7 | 14 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
373 | ID0373 | ODC-D8 | 14.125 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
374 | ID0374 | ODC-D9 | 14.25 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
375 | ID0375 | ODC-D10 | 14.375 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
376 | ID0376 | ODC-D11 | 14.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
377 | ID0377 | ODC-D12 | 14.625 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
378 | ID0378 | ODC-D13 | 14.75 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
379 | ID0379 | ODC-D14 | 14.875 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
380 | ID0380 | ODC-D15 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
381 | ID0381 | ODC-D16 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
382 | ID0382 | ODC-D17 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
383 | ID0383 | ODC-E1 | 14 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
384 | ID0384 | ODC-E2 | 14.0833 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
385 | ID0385 | ODC-E3 | 14.1667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
386 | ID0386 | ODC-E4 | 14.25 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
387 | ID0387 | ODC-E5 | 14.3333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
388 | ID0388 | ODC-E6 | 14.4167 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
389 | ID0389 | ODC-E7 | 14.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
390 | ID0390 | ODC-E8 | 14.5625 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
391 | ID0391 | ODC-E9 | 14.625 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
392 | ID0392 | ODC-E10 | 14.6875 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
393 | ID0393 | ODC-E11 | 14.75 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
394 | ID0394 | ODC-E12 | 14.8125 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
395 | ID0395 | ODC-E13 | 14.875 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
396 | ID0396 | ODC-E14 | 14.9375 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
397 | ID0397 | ODC-E15 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
398 | ID0398 | ODC-E16 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
399 | ID0399 | ODC-E17 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
400 | ID0400 | ODC-F1 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
401 | ID0401 | ODC-F2 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
402 | ID0402 | ODC-F3 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
403 | ID0403 | ODC-F4 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
404 | ID0404 | ODC-F5 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
405 | ID0405 | ODC-F6 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
406 | ID0406 | ODC-F7 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
407 | ID0407 | ODC-F8 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
408 | ID0408 | ODC-F9 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
409 | ID0409 | ODC-F10 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
410 | ID0410 | ODC-F11 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
411 | ID0411 | ODC-F12 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
412 | ID0412 | ODC-F13 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
413 | ID0413 | ODC-F14 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
414 | ID0414 | ODC-F15 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
415 | ID0415 | ODC-F16 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
416 | ID0416 | ODC-G1 | 15 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
417 | ID0417 | ODC-G2 | 16 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
418 | ID0418 | ODC-G3 | 16 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
419 | ID0419 | ODC-G4 | 16 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
420 | ID0420 | ODC-G5 | 16 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
421 | ID0421 | ODC-G6 | 16 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
422 | ID0422 | ODC-G7 | 16 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
423 | ID0423 | ODC-G8 | 16 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
424 | ID0424 | ODC-G9 | 16 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
425 | ID0425 | ODC-G10 | 16 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
426 | ID0426 | ODC-G11 | 16 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
427 | ID0427 | ODC-G12 | 16 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
428 | ID0428 | ODC-G13 | 16 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
429 | ID0429 | ODC-G14 | 16 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
430 | ID0430 | ODC-G15 | 16 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
431 | ID0431 | ODC-G16 | 16 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
432 | ID0432 | ODC-G17 | 16 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
433 | ID0433 | ODC-H1 | 16 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
434 | ID0434 | ODC-H2 | 13 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
435 | ID0435 | ODC-H3 | 14.3333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
436 | ID0436 | ODC-H4 | 15.6667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
437 | ID0437 | ODC-H5 | 17 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
438 | ID0438 | ODC-H6 | 18.3333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
439 | ID0439 | ODC-H7 | 19.6667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
440 | ID0440 | ODC-H8 | 21 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
441 | ID0441 | ODC-H9 | 21.25 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
442 | ID0442 | ODC-H10 | 21.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
443 | ID0443 | ODC-H11 | 21.75 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
444 | ID0444 | ODC-H12 | 22 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
445 | ID0445 | ODC-H13 | 22.25 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
446 | ID0446 | ODC-H14 | 22.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
447 | ID0447 | ODC-H15 | 22.75 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
448 | ID0448 | ODC-H16 | 23 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
449 | ID0449 | ODC-H17 | 23.25 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
450 | ID0450 | ODC-I1 | 23.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
451 | ID0451 | ODC-I2 | 14.6667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
452 | ID0452 | ODC-I3 | 15.4333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
453 | ID0453 | ODC-I4 | 16.7667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
454 | ID0454 | ODC-I5 | 18.1 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
455 | ID0455 | ODC-I6 | 19.4333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
456 | ID0456 | ODC-I7 | 20.7667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
457 | ID0457 | ODC-I8 | 21.3333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
458 | ID0458 | ODC-I9 | 21.6333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
459 | ID0459 | ODC-I10 | 21.9333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
460 | ID0460 | ODC-I11 | 22.2333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
461 | ID0461 | ODC-I12 | 22.5333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
462 | ID0462 | ODC-I13 | 22.8333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
463 | ID0463 | ODC-I14 | 23.1333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
464 | ID0464 | ODC-I15 | 23.4333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
465 | ID0465 | ODC-I16 | 23.6667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
466 | ID0466 | ODC-I17 | 24 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
467 | ID0467 | ODC-J1 | 24.3 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
468 | ID0468 | ODC-J2 | 16.3333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
469 | ID0469 | ODC-J3 | 17.2333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
470 | ID0470 | ODC-J4 | 18.1333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
471 | ID0471 | ODC-J5 | 19.0333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
472 | ID0472 | ODC-J6 | 19.9333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
473 | ID0473 | ODC-J7 | 20.8333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
474 | ID0474 | ODC-J8 | 21.6667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
475 | ID0475 | ODC-J9 | 21.9917 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
476 | ID0476 | ODC-J10 | 22.3167 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
477 | ID0477 | ODC-J11 | 22.6417 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
478 | ID0478 | ODC-J12 | 22.9667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
479 | ID0479 | ODC-J13 | 23.2917 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
480 | ID0480 | ODC-J14 | 23.6167 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
481 | ID0481 | ODC-J15 | 23.9417 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
482 | ID0482 | ODC-J16 | 24.3333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
483 | ID0483 | ODC-J17 | 24.7 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
484 | ID0484 | ODC-J18 | 25.1 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
485 | ID0485 | ODC-K1 | 18 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
486 | ID0486 | ODC-K2 | 18.6667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
487 | ID0487 | ODC-K3 | 19.3333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
488 | ID0488 | ODC-K4 | 20 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
489 | ID0489 | ODC-K5 | 20.6667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
490 | ID0490 | ODC-K6 | 21.3333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
491 | ID0491 | ODC-K7 | 22 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
492 | ID0492 | ODC-K8 | 22.375 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
493 | ID0493 | ODC-K9 | 22.75 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
494 | ID0494 | ODC-K10 | 23.125 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
495 | ID0495 | ODC-K11 | 23.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
496 | ID0496 | ODC-K12 | 23.875 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
497 | ID0497 | ODC-K13 | 24.25 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
498 | ID0498 | ODC-K14 | 24.625 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
499 | ID0499 | ODC-K15 | 25 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
500 | ID0500 | ODC-K16 | 25.37 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
501 | ID0501 | ODC-K17 | 25.74 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
502 | ID0502 | ODC-L1 | 19 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
503 | ID0503 | ODC-L2 | 19.6667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
504 | ID0504 | ODC-L3 | 20.3333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
505 | ID0505 | ODC-L4 | 21 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
506 | ID0506 | ODC-L5 | 21.6667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
507 | ID0507 | ODC-L6 | 22.3333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
508 | ID0508 | ODC-L7 | 23 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
509 | ID0509 | ODC-L8 | 23.375 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
510 | ID0510 | ODC-L9 | 23.75 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
511 | ID0511 | ODC-L10 | 24.125 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
512 | ID0512 | ODC-L11 | 24.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
513 | ID0513 | ODC-L12 | 24.875 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
514 | ID0514 | ODC-L13 | 25.25 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
515 | ID0515 | ODC-L14 | 25.625 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
516 | ID0516 | ODC-L15 | 26 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
517 | ID0517 | ODC-L16 | 26.31 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
518 | ID0518 | ODC-L17 | 26.62 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
519 | ID0519 | ODC-M1 | 20 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
520 | ID0520 | ODC-M2 | 20.6667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
521 | ID0521 | ODC-M3 | 21.3333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
522 | ID0522 | ODC-M4 | 22 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
523 | ID0523 | ODC-M5 | 22.6667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
524 | ID0524 | ODC-M6 | 23.3333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
525 | ID0525 | ODC-M7 | 24 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
526 | ID0526 | ODC-M8 | 24.375 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
527 | ID0527 | ODC-M9 | 24.75 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
528 | ID0528 | ODC-M10 | 25.125 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
529 | ID0529 | ODC-M11 | 25.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
530 | ID0530 | ODC-M12 | 25.875 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
531 | ID0531 | ODC-M13 | 26.25 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
532 | ID0532 | ODC-M14 | 26.625 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
533 | ID0533 | ODC-M15 | 27 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
534 | ID0534 | ODC-M16 | 27.37 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
535 | ID0535 | ODC-M17 | 27.74 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
536 | ID0536 | ODC-N1 | 21 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
537 | ID0537 | ODC-N2 | 21.6667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
538 | ID0538 | ODC-N3 | 22.3333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
539 | ID0539 | ODC-N4 | 23 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
540 | ID0540 | ODC-N5 | 23.6667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
541 | ID0541 | ODC-N6 | 24.3333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
542 | ID0542 | ODC-N7 | 25 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
543 | ID0543 | ODC-N8 | 25.375 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
544 | ID0544 | ODC-N9 | 25.75 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
545 | ID0545 | ODC-N10 | 26.125 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
546 | ID0546 | ODC-N11 | 26.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
547 | ID0547 | ODC-N12 | 26.875 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
548 | ID0548 | ODC-N13 | 27.25 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
549 | ID0549 | ODC-N14 | 27.625 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
550 | ID0550 | ODC-N15 | 28 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
551 | ID0551 | ODC-N16 | 28.37 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
552 | ID0552 | ODC-N17 | 28.74 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
553 | ID0553 | ODH-A1 | 18 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
554 | ID0554 | ODH-A2 | 19.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
555 | ID0555 | ODH-A3 | 21 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
556 | ID0556 | ODH-A4 | 22.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
557 | ID0557 | ODH-A5 | 24 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
558 | ID0558 | ODH-A6 | 25.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
559 | ID0559 | ODH-A7 | 27 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
560 | ID0560 | ODH-A8 | 26.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
561 | ID0561 | ODH-A9 | 26 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
562 | ID0562 | ODH-A10 | 25.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
563 | ID0563 | ODH-A11 | 25 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
564 | ID0564 | ODH-A12 | 24.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
565 | ID0565 | ODH-A13 | 24 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
566 | ID0566 | ODH-A14 | 23.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
567 | ID0567 | ODH-A15 | 23 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
568 | ID0568 | ODH-A16 | 23 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
569 | ID0569 | ODH-A17 | 23 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
570 | ID0570 | ODH-B1 | 18 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
571 | ID0571 | ODH-B2 | 19 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
572 | ID0572 | ODH-B3 | 20 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
573 | ID0573 | ODH-B4 | 21 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
574 | ID0574 | ODH-B5 | 22 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
575 | ID0575 | ODH-B6 | 23 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
576 | ID0576 | ODH-B7 | 24 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
577 | ID0577 | ODH-B8 | 23.625 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
578 | ID0578 | ODH-B9 | 23.25 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
579 | ID0579 | ODH-B10 | 22.875 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
580 | ID0580 | ODH-B11 | 22.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
581 | ID0581 | ODH-B12 | 22.125 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
582 | ID0582 | ODH-B13 | 21.75 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
583 | ID0583 | ODH-B14 | 21.375 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
584 | ID0584 | ODH-B15 | 21 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
585 | ID0585 | ODH-B16 | 21 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
586 | ID0586 | ODH-B17 | 21 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
587 | ID0587 | ODH-C1 | 18 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
588 | ID0588 | ODH-C2 | 18.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
589 | ID0589 | ODH-C3 | 19 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
590 | ID0590 | ODH-C4 | 19.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
591 | ID0591 | ODH-C5 | 20 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
592 | ID0592 | ODH-C6 | 21 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
593 | ID0593 | ODH-C7 | 21 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
594 | ID0594 | ODH-C8 | 20.75 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
595 | ID0595 | ODH-C9 | 20.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
596 | ID0596 | ODH-C10 | 20.25 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
597 | ID0597 | ODH-C11 | 20 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
598 | ID0598 | ODH-C12 | 19.75 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
599 | ID0599 | ODH-C13 | 19.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
600 | ID0600 | ODH-C14 | 19.25 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
601 | ID0601 | ODH-C15 | 19 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
602 | ID0602 | ODH-C16 | 19 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
603 | ID0603 | ODH-C17 | 19 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
604 | ID0604 | ODH-D1 | 18 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
605 | ID0605 | ODH-D2 | 18 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
606 | ID0606 | ODH-D3 | 18 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
607 | ID0607 | ODH-D4 | 18 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
608 | ID0608 | ODH-D5 | 18 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
609 | ID0609 | ODH-D6 | 18 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
610 | ID0610 | ODH-D7 | 18 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
611 | ID0611 | ODH-D8 | 17.875 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
612 | ID0612 | ODH-D9 | 17.75 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
613 | ID0613 | ODH-D10 | 17.625 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
614 | ID0614 | ODH-D11 | 17.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
615 | ID0615 | ODH-D12 | 17.375 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
616 | ID0616 | ODH-D13 | 17.25 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
617 | ID0617 | ODH-D14 | 17.125 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
618 | ID0618 | ODH-D15 | 17 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
619 | ID0619 | ODH-D16 | 17 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
620 | ID0620 | ODH-D17 | 17 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
621 | ID0621 | ODH-E1 | 17.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
622 | ID0622 | ODH-E2 | 17.4 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
623 | ID0623 | ODH-E3 | 17.3 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
624 | ID0624 | ODH-E4 | 17.3 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
625 | ID0625 | ODH-E5 | 17.2 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
626 | ID0626 | ODH-E6 | 17 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
627 | ID0627 | ODH-E7 | 17 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
628 | ID0628 | ODH-E8 | 16.8 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
629 | ID0629 | ODH-E9 | 16.8 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
630 | ID0630 | ODH-E10 | 16.8 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
631 | ID0631 | ODH-E11 | 16.7 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
632 | ID0632 | ODH-E12 | 16.6875 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
633 | ID0633 | ODH-E13 | 16.625 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
634 | ID0634 | ODH-E14 | 16.5625 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
635 | ID0635 | ODH-E15 | 16.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
636 | ID0636 | ODH-E16 | 16.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
637 | ID0637 | ODH-E17 | 16.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
638 | ID0638 | ODH-F1 | 17 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
639 | ID0639 | ODH-F2 | 16.8333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
640 | ID0640 | ODH-F3 | 16.6667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
641 | ID0641 | ODH-F4 | 16.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
642 | ID0642 | ODH-F5 | 16.3333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
643 | ID0643 | ODH-F6 | 16.1667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
644 | ID0644 | ODH-F7 | 16 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
645 | ID0645 | ODH-F8 | 16 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
646 | ID0646 | ODH-F9 | 16 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
647 | ID0647 | ODH-F10 | 16 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
648 | ID0648 | ODH-F11 | 16 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
649 | ID0649 | ODH-F12 | 16 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
650 | ID0650 | ODH-F13 | 16 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
651 | ID0651 | ODH-F14 | 16 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
652 | ID0652 | ODH-F15 | 16 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
653 | ID0653 | ODH-F16 | 16 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
654 | ID0654 | ODH-F17 | 16 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
655 | ID0655 | ODH-G1 | 27 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
656 | ID0656 | ODH-G2 | 28.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
657 | ID0657 | ODH-G3 | 30 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
658 | ID0658 | ODH-G4 | 31.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
659 | ID0659 | ODH-G5 | 33 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
660 | ID0660 | ODH-G6 | 34.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
661 | ID0661 | ODH-G7 | 36 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
662 | ID0662 | ODH-G8 | 36.25 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
663 | ID0663 | ODH-G9 | 36.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
664 | ID0664 | ODH-G10 | 36.75 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
665 | ID0665 | ODH-G11 | 37 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
666 | ID0666 | ODH-G12 | 37.25 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
667 | ID0667 | ODH-G13 | 37.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
668 | ID0668 | ODH-G14 | 37.75 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
669 | ID0669 | ODH-G15 | 38 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
670 | ID0670 | ODH-G16 | 38 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
671 | ID0671 | ODH-G17 | 38 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
672 | ID0672 | ODH-H1 | 25.6667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
673 | ID0673 | ODH-H2 | 27 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
674 | ID0674 | ODH-H3 | 28.3333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
675 | ID0675 | ODH-H4 | 29.6667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
676 | ID0676 | ODH-H5 | 31 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
677 | ID0677 | ODH-H6 | 32.3333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
678 | ID0678 | ODH-H7 | 33.6667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
679 | ID0679 | ODH-H8 | 33.9583 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
680 | ID0680 | ODH-H9 | 34.25 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
681 | ID0681 | ODH-H10 | 34.5417 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
682 | ID0682 | ODH-H11 | 34.8333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
683 | ID0683 | ODH-H12 | 35.125 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
684 | ID0684 | ODH-H13 | 35.4167 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
685 | ID0685 | ODH-H14 | 35.7083 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
686 | ID0686 | ODH-H15 | 36 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
687 | ID0687 | ODH-H16 | 36 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
688 | ID0688 | ODH-H17 | 36 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
689 | ID0689 | ODH-I1 | 24.3333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
690 | ID0690 | ODH-I2 | 25.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
691 | ID0691 | ODH-I3 | 26.6667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
692 | ID0692 | ODH-I4 | 27.8333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
693 | ID0693 | ODH-I5 | 29 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
694 | ID0694 | ODH-I6 | 30.1667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
695 | ID0695 | ODH-I7 | 31.3333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
696 | ID0696 | ODH-I8 | 31.6667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
697 | ID0697 | ODH-I9 | 32 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
698 | ID0698 | ODH-I10 | 32.3333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
699 | ID0699 | ODH-I11 | 32.6667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
700 | ID0700 | ODH-I12 | 33 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
701 | ID0701 | ODH-I13 | 33.3333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
702 | ID0702 | ODH-I14 | 33.6667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
703 | ID0703 | ODH-I15 | 34 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
704 | ID0704 | ODH-I16 | 34 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
705 | ID0705 | ODH-I17 | 34 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
706 | ID0706 | ODH-J1 | 23 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
707 | ID0707 | ODH-J2 | 24 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
708 | ID0708 | ODH-J3 | 25 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
709 | ID0709 | ODH-J4 | 26 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
710 | ID0710 | ODH-J5 | 27 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
711 | ID0711 | ODH-J6 | 28 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
712 | ID0712 | ODH-J7 | 29 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
713 | ID0713 | ODH-J8 | 29.375 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
714 | ID0714 | ODH-J9 | 29.75 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
715 | ID0715 | ODH-J10 | 30.125 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
716 | ID0716 | ODH-J11 | 30.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
717 | ID0717 | ODH-J12 | 30.875 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
718 | ID0718 | ODH-J13 | 31.25 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
719 | ID0719 | ODH-J14 | 31.625 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
720 | ID0720 | ODH-J15 | 32 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
721 | ID0721 | ODH-J16 | 32.375 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
722 | ID0722 | ODH-J17 | 32.75 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
723 | ID0723 | ODH-K1 | 22.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
724 | ID0724 | ODH-K2 | 23.4 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
725 | ID0725 | ODH-K3 | 24 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
726 | ID0726 | ODH-K4 | 25 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
727 | ID0727 | ODH-K5 | 25.6 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
728 | ID0728 | ODH-K6 | 26.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
729 | ID0729 | ODH-K7 | 27.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
730 | ID0730 | ODH-K8 | 27.8125 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
731 | ID0731 | ODH-K9 | 28.125 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
732 | ID0732 | ODH-K10 | 28.4375 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
733 | ID0733 | ODH-K11 | 28.75 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
734 | ID0734 | ODH-K12 | 29.0625 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
735 | ID0735 | ODH-K13 | 29.375 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
736 | ID0736 | ODH-K14 | 29.6875 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
737 | ID0737 | ODH-K15 | 30 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
738 | ID0738 | ODH-K16 | 30 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
739 | ID0739 | ODH-K17 | 30 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
740 | ID0740 | ODH-L1 | 22 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
741 | ID0741 | ODH-L2 | 22.6667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
742 | ID0742 | ODH-L3 | 23.3333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
743 | ID0743 | ODH-L4 | 24 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
744 | ID0744 | ODH-L5 | 24.6667 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
745 | ID0745 | ODH-L6 | 25.3333 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
746 | ID0746 | ODH-L7 | 26 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
747 | ID0747 | ODH-L8 | 26.25 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
748 | ID0748 | ODH-L9 | 26.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
749 | ID0749 | ODH-L10 | 26.75 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
750 | ID0750 | ODH-L11 | 27 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
751 | ID0751 | ODH-L12 | 27.25 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
752 | ID0752 | ODH-L13 | 27.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
753 | ID0753 | ODH-L14 | 27.75 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
754 | ID0754 | ODH-L15 | 28 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
755 | ID0755 | ODH-L16 | 28.25 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
756 | ID0756 | ODH-L17 | 28.5 | 0 | 60 | 0 | YES | 0.1 | 0 | R&D
757 | ID0757 | ODH-LRPS (30) | 30 | 0 | 90 | 0 | YES | 1 | 0 | R&D
758 | ID0758 | SOR act time (60) | 60 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
759 | ID0759 | SOR rec time (60) | 60 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
760 | ID0760 | SOR rec max time ( 5 ) | 5 min | 0 | 60 | 0 | YES | 1 | 0 | R&D
761 | ID0761 | SOR fail detect time (3) | 3 min | 0 | 30 | 0 | YES | 1 | 0 | R&D
762 | ID0762 | SOR OSR rps (60) | 60 | 0 | 90 | 0 | YES | 1 | 0 | R&D
763 | ID0763 | SOR OSR time (3) | 3 min | 0 | 30 | 0 | YES | 1 | 0 | R&D
764 | ID0764 | oil swap timer after power on (120) | 120 min | 0 | 900 | 0 | YES | 1 | 0 | R&D
765 | ID0765 | oil swap timer after thermo on (720) | 720 min | 0 | 900 | 0 | YES | 1 | 0 | R&D
766 | ID0766 | OSWLC-A0 | 60 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
767 | ID0767 | OSWLC-A1 | 65 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
768 | ID0768 | OSWLC-A2 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
769 | ID0769 | OSWLC-A3 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
770 | ID0770 | OSWLC-A4 | 65 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
771 | ID0771 | OSWLC-A5 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
772 | ID0772 | OSWLC-A6 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
773 | ID0773 | OSWLC-A7 | 65 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
774 | ID0774 | OSWLC-A8 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
775 | ID0775 | OSWLC-A9 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
776 | ID0776 | OSWLC-A10 | 65 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
777 | ID0777 | OSWLC-A11 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
778 | ID0778 | OSWLC-A12 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
779 | ID0779 | OSWLC-B0 | 90sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
780 | ID0780 | OSWLC-B1 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
781 | ID0781 | OSWLC-B2 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
782 | ID0782 | OSWLC-B3 | ON | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
783 | ID0783 | OSWLC-B4 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
784 | ID0784 | OSWLC-B5 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
785 | ID0785 | OSWLC-B6 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
786 | ID0786 | OSWLC-B7 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
787 | ID0787 | OSWLC-B8 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
788 | ID0788 | OSWLC-B9 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
789 | ID0789 | OSWLC-B10 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
790 | ID0790 | OSWLC-B11 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
791 | ID0791 | OSWLC-B12 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
792 | ID0792 | OSWLC-C0 | 90sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
793 | ID0793 | OSWLC-C1 | 30 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
794 | ID0794 | OSWLC-C2 | ON | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
795 | ID0795 | OSWLC-C3 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
796 | ID0796 | OSWLC-C4 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
797 | ID0797 | OSWLC-C5 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
798 | ID0798 | OSWLC-C6 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
799 | ID0799 | OSWLC-C7 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
800 | ID0800 | OSWLC-C8 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
801 | ID0801 | OSWLC-C9 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
802 | ID0802 | OSWLC-C10 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
803 | ID0803 | OSWLC-C11 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
804 | ID0804 | OSWLC-C12 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
805 | ID0805 | OSWLC-D0 | 90sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
806 | ID0806 | OSWLC-D1 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
807 | ID0807 | OSWLC-D2 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
808 | ID0808 | OSWLC-D3 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
809 | ID0809 | OSWLC-D4 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
810 | ID0810 | OSWLC-D5 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
811 | ID0811 | OSWLC-D6 | ON | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
812 | ID0812 | OSWLC-D7 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
813 | ID0813 | OSWLC-D8 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
814 | ID0814 | OSWLC-D9 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
815 | ID0815 | OSWLC-D10 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
816 | ID0816 | OSWLC-D11 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
817 | ID0817 | OSWLC-D12 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
818 | ID0818 | OSWLC-E0 | 90sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
819 | ID0819 | OSWLC-E1 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
820 | ID0820 | OSWLC-E2 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
821 | ID0821 | OSWLC-E3 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
822 | ID0822 | OSWLC-E4 | 30 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
823 | ID0823 | OSWLC-E5 | ON | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
824 | ID0824 | OSWLC-E6 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
825 | ID0825 | OSWLC-E7 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
826 | ID0826 | OSWLC-E8 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
827 | ID0827 | OSWLC-E9 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
828 | ID0828 | OSWLC-E10 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
829 | ID0829 | OSWLC-E11 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
830 | ID0830 | OSWLC-E12 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
831 | ID0831 | OSWLC-F0 | 90sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
832 | ID0832 | OSWLC-F1 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
833 | ID0833 | OSWLC-F2 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
834 | ID0834 | OSWLC-F3 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
835 | ID0835 | OSWLC-F4 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
836 | ID0836 | OSWLC-F5 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
837 | ID0837 | OSWLC-F6 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
838 | ID0838 | OSWLC-F7 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
839 | ID0839 | OSWLC-F8 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
840 | ID0840 | OSWLC-F9 | ON | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
841 | ID0841 | OSWLC-F10 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
842 | ID0842 | OSWLC-F11 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
843 | ID0843 | OSWLC-F12 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
844 | ID0844 | OSWLC-G0 | 90sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
845 | ID0845 | OSWLC-G1 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
846 | ID0846 | OSWLC-G2 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
847 | ID0847 | OSWLC-G3 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
848 | ID0848 | OSWLC-G4 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
849 | ID0849 | OSWLC-G5 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
850 | ID0850 | OSWLC-G6 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
851 | ID0851 | OSWLC-G7 | 30 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
852 | ID0852 | OSWLC-G8 | ON | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
853 | ID0853 | OSWLC-G9 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
854 | ID0854 | OSWLC-G10 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
855 | ID0855 | OSWLC-G11 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
856 | ID0856 | OSWLC-G12 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
857 | ID0857 | OSWLC-H0 | 90sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
858 | ID0858 | OSWLC-H1 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
859 | ID0859 | OSWLC-H2 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
860 | ID0860 | OSWLC-H3 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
861 | ID0861 | OSWLC-H4 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
862 | ID0862 | OSWLC-H5 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
863 | ID0863 | OSWLC-H6 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
864 | ID0864 | OSWLC-H7 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
865 | ID0865 | OSWLC-H8 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
866 | ID0866 | OSWLC-H9 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
867 | ID0867 | OSWLC-H10 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
868 | ID0868 | OSWLC-H11 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
869 | ID0869 | OSWLC-H12 | ON | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
870 | ID0870 | OSWLC-I0 | 90sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
871 | ID0871 | OSWLC-I1 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
872 | ID0872 | OSWLC-I2 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
873 | ID0873 | OSWLC-I3 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
874 | ID0874 | OSWLC-I4 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
875 | ID0875 | OSWLC-I5 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
876 | ID0876 | OSWLC-I6 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
877 | ID0877 | OSWLC-I7 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
878 | ID0878 | OSWLC-I8 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
879 | ID0879 | OSWLC-I9 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
880 | ID0880 | OSWLC-I10 | 30 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
881 | ID0881 | OSWLC-I11 | ON | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
882 | ID0882 | OSWLC-I12 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
883 | ID0883 | OSWLC-J0 | 60sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
884 | ID0884 | OSWLC-J1 | 30 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
885 | ID0885 | OSWLC-J2 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
886 | ID0886 | OSWLC-J3 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
887 | ID0887 | OSWLC-J4 | 30 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
888 | ID0888 | OSWLC-J5 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
889 | ID0889 | OSWLC-J6 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
890 | ID0890 | OSWLC-J7 | 30 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
891 | ID0891 | OSWLC-J8 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
892 | ID0892 | OSWLC-J9 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
893 | ID0893 | OSWLC-J10 | 30 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
894 | ID0894 | OSWLC-J11 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
895 | ID0895 | OSWLC-J12 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
896 | ID0896 | OSWLH-A0 | 60 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
897 | ID0897 | OSWLH-A1 | 65 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
898 | ID0898 | OSWLH-A2 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
899 | ID0899 | OSWLH-A3 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
900 | ID0900 | OSWLH-A4 | 65 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
901 | ID0901 | OSWLH-A5 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
902 | ID0902 | OSWLH-A6 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
903 | ID0903 | OSWLH-A7 | 65 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
904 | ID0904 | OSWLH-A8 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
905 | ID0905 | OSWLH-A9 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
906 | ID0906 | OSWLH-A10 | 65 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
907 | ID0907 | OSWLH-A11 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
908 | ID0908 | OSWLH-A12 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
909 | ID0909 | OSWLH-A13 | 300 | 0 | 480 | 0 | YES | 1 | 0 | R&D
910 | ID0910 | OSWLH-B0 | 90 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
911 | ID0911 | OSWLH-B1 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
912 | ID0912 | OSWLH-B2 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
913 | ID0913 | OSWLH-B3 | ON | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
914 | ID0914 | OSWLH-B4 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
915 | ID0915 | OSWLH-B5 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
916 | ID0916 | OSWLH-B6 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
917 | ID0917 | OSWLH-B7 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
918 | ID0918 | OSWLH-B8 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
919 | ID0919 | OSWLH-B9 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
920 | ID0920 | OSWLH-B10 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
921 | ID0921 | OSWLH-B11 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
922 | ID0922 | OSWLH-B12 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
923 | ID0923 | OSWLH-B13 | 300 | 0 | 480 | 0 | YES | 1 | 0 | R&D
924 | ID0924 | OSWLH-C0 | 90 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
925 | ID0925 | OSWLH-C1 | 30 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
926 | ID0926 | OSWLH-C2 | ON | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
927 | ID0927 | OSWLH-C3 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
928 | ID0928 | OSWLH-C4 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
929 | ID0929 | OSWLH-C5 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
930 | ID0930 | OSWLH-C6 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
931 | ID0931 | OSWLH-C7 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
932 | ID0932 | OSWLH-C8 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
933 | ID0933 | OSWLH-C9 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
934 | ID0934 | OSWLH-C10 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
935 | ID0935 | OSWLH-C11 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
936 | ID0936 | OSWLH-C12 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
937 | ID0937 | OSWLH-C13 | 300 | 0 | 480 | 0 | YES | 1 | 0 | R&D
938 | ID0938 | OSWLH-D0 | 90 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
939 | ID0939 | OSWLH-D1 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
940 | ID0940 | OSWLH-D2 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
941 | ID0941 | OSWLH-D3 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
942 | ID0942 | OSWLH-D4 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
943 | ID0943 | OSWLH-D5 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
944 | ID0944 | OSWLH-D6 | ON | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
945 | ID0945 | OSWLH-D7 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
946 | ID0946 | OSWLH-D8 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
947 | ID0947 | OSWLH-D9 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
948 | ID0948 | OSWLH-D10 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
949 | ID0949 | OSWLH-D11 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
950 | ID0950 | OSWLH-D12 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
951 | ID0951 | OSWLH-D13 | 300 | 0 | 480 | 0 | YES | 1 | 0 | R&D
952 | ID0952 | OSWLH-E0 | 90 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
953 | ID0953 | OSWLH-E1 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
954 | ID0954 | OSWLH-E2 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
955 | ID0955 | OSWLH-E3 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
956 | ID0956 | OSWLH-E4 | 30 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
957 | ID0957 | OSWLH-E5 | ON | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
958 | ID0958 | OSWLH-E6 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
959 | ID0959 | OSWLH-E7 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
960 | ID0960 | OSWLH-E8 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
961 | ID0961 | OSWLH-E9 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
962 | ID0962 | OSWLH-E10 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
963 | ID0963 | OSWLH-E11 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
964 | ID0964 | OSWLH-E12 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
965 | ID0965 | OSWLH-E13 | 300 | 0 | 480 | 0 | YES | 1 | 0 | R&D
966 | ID0966 | OSWLH-F0 | 90 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
967 | ID0967 | OSWLH-F1 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
968 | ID0968 | OSWLH-F2 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
969 | ID0969 | OSWLH-F3 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
970 | ID0970 | OSWLH-F4 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
971 | ID0971 | OSWLH-F5 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
972 | ID0972 | OSWLH-F6 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
973 | ID0973 | OSWLH-F7 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
974 | ID0974 | OSWLH-F8 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
975 | ID0975 | OSWLH-F9 | ON | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
976 | ID0976 | OSWLH-F10 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
977 | ID0977 | OSWLH-F11 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
978 | ID0978 | OSWLH-F12 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
979 | ID0979 | OSWLH-F13 | 300 | 0 | 480 | 0 | YES | 1 | 0 | R&D
980 | ID0980 | OSWLH-G0 | 90 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
981 | ID0981 | OSWLH-G1 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
982 | ID0982 | OSWLH-G2 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
983 | ID0983 | OSWLH-G3 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
984 | ID0984 | OSWLH-G4 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
985 | ID0985 | OSWLH-G5 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
986 | ID0986 | OSWLH-G6 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
987 | ID0987 | OSWLH-G7 | 30 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
988 | ID0988 | OSWLH-G8 | ON | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
989 | ID0989 | OSWLH-G9 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
990 | ID0990 | OSWLH-G10 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
991 | ID0991 | OSWLH-G11 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
992 | ID0992 | OSWLH-G12 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
993 | ID0993 | OSWLH-G13 | 300 | 0 | 480 | 0 | YES | 1 | 0 | R&D
994 | ID0994 | OSWLH-H0 | 90 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
995 | ID0995 | OSWLH-H1 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
996 | ID0996 | OSWLH-H2 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
997 | ID0997 | OSWLH-H3 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
998 | ID0998 | OSWLH-H4 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
999 | ID0999 | OSWLH-H5 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
1000 | ID1000 | OSWLH-H6 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
1001 | ID1001 | OSWLH-H7 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1002 | ID1002 | OSWLH-H8 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
1003 | ID1003 | OSWLH-H9 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
1004 | ID1004 | OSWLH-H10 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1005 | ID1005 | OSWLH-H11 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
1006 | ID1006 | OSWLH-H12 | ON | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
1007 | ID1007 | OSWLH-H13 | 300 | 0 | 480 | 0 | YES | 1 | 0 | R&D
1008 | ID1008 | OSWLH-I0 | 90 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
1009 | ID1009 | OSWLH-I1 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1010 | ID1010 | OSWLH-I2 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
1011 | ID1011 | OSWLH-I3 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
1012 | ID1012 | OSWLH-I4 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1013 | ID1013 | OSWLH-I5 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
1014 | ID1014 | OSWLH-I6 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
1015 | ID1015 | OSWLH-I7 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1016 | ID1016 | OSWLH-I8 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
1017 | ID1017 | OSWLH-I9 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
1018 | ID1018 | OSWLH-I10 | 30 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1019 | ID1019 | OSWLH-I11 | ON | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
1020 | ID1020 | OSWLH-I12 | OFF | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
1021 | ID1021 | OSWLH-I13 | 300 | 0 | 480 | 0 | YES | 1 | 0 | R&D
1022 | ID1022 | OSWLH-J0 | 60 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
1023 | ID1023 | OSWLH-J1 | 30 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1024 | ID1024 | OSWLH-J2 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
1025 | ID1025 | OSWLH-J3 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
1026 | ID1026 | OSWLH-J4 | 30 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1027 | ID1027 | OSWLH-J5 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
1028 | ID1028 | OSWLH-J6 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
1029 | ID1029 | OSWLH-J7 | 30 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1030 | ID1030 | OSWLH-J8 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
1031 | ID1031 | OSWLH-J9 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
1032 | ID1032 | OSWLH-J10 | 30 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1033 | ID1033 | OSWLH-J11 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
1034 | ID1034 | OSWLH-J12 | NC | ON | OFF | 0 | YES | ON/OFF/Normal Control | 0 | R&D
1035 | ID1035 | OSWLH-J13 | 300 | 0 | 480 | 0 | YES | 1 | 0 | R&D
1036 | ID1036 | Oil Swap Time | 3 min | 0 | 60 | 0 | YES | 1 | 0 | R&D
1037 | ID1037 | OSLC-A0 | 60 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
1038 | ID1038 | OSLC-A1 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1039 | ID1039 | OSLC-A2 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1040 | ID1040 | OSLC-A3 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1041 | ID1041 | OSLC-A4 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1042 | ID1042 | OSLC-B0 | 30 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
1043 | ID1043 | OSLC-B1 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1044 | ID1044 | OSLC-B2 | 40 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1045 | ID1045 | OSLC-B3 | 65 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1046 | ID1046 | OSLC-B4 | 65 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1047 | ID1047 | OSLC-C0 | 30 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
1048 | ID1048 | OSLC-C1 | 40 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1049 | ID1049 | OSLC-C2 | 65 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1050 | ID1050 | OSLC-C3 | 65 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1051 | ID1051 | OSLC-C4 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1052 | ID1052 | OSLC-D0 | 30 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
1053 | ID1053 | OSLC-D1 | 65 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1054 | ID1054 | OSLC-D2 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1055 | ID1055 | OSLC-D3 | 40 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1056 | ID1056 | OSLC-D4 | 65 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1057 | ID1057 | OSLC-E0 | 30 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
1058 | ID1058 | OSLC-E1 | 65 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1059 | ID1059 | OSLC-E2 | 65 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1060 | ID1060 | OSLC-E3 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1061 | ID1061 | OSLC-E4 | 40 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1062 | ID1062 | OSLC-F0 | 60 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
1063 | ID1063 | OSLC-F1 | 30 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1064 | ID1064 | OSLC-F2 | 30 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1065 | ID1065 | OSLC-F3 | 30 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1066 | ID1066 | OSLC-F4 | 30 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1067 | ID1067 | OSLH-A0 | 60 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
1068 | ID1068 | OSLH-A1 | 20 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1069 | ID1069 | OSLH-A2 | 20 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1070 | ID1070 | OSLH-A3 | 20 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1071 | ID1071 | OSLH-A4 | 20 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1072 | ID1072 | OSLH-A5 | 300 | 0 | 480 | 0 | YES | 1 | 0 | R&D
1073 | ID1073 | OSLH-B0 | 30 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
1074 | ID1074 | OSLH-B1 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1075 | ID1075 | OSLH-B2 | 20 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1076 | ID1076 | OSLH-B3 | 20 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1077 | ID1077 | OSLH-B4 | 20 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1078 | ID1078 | OSLH-B5 | 300 | 0 | 480 | 0 | YES | 1 | 0 | R&D
1079 | ID1079 | OSLH-C0 | 30 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
1080 | ID1080 | OSLH-C1 | 20 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1081 | ID1081 | OSLH-C2 | 20 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1082 | ID1082 | OSLH-C3 | 20 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1083 | ID1083 | OSLH-C4 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1084 | ID1084 | OSLH-C5 | 300 | 0 | 480 | 0 | YES | 1 | 0 | R&D
1085 | ID1085 | OSLH-D0 | 30 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
1086 | ID1086 | OSLH-D1 | 20 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1087 | ID1087 | OSLH-D2 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1088 | ID1088 | OSLH-D3 | 20 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1089 | ID1089 | OSLH-D4 | 20 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1090 | ID1090 | OSLH-D5 | 300 | 0 | 480 | 0 | YES | 1 | 0 | R&D
1091 | ID1091 | OSLH-E0 | 30 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
1092 | ID1092 | OSLH-E1 | 20 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1093 | ID1093 | OSLH-E2 | 20 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1094 | ID1094 | OSLH-E3 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1095 | ID1095 | OSLH-E4 | 20 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1096 | ID1096 | OSLH-E5 | 300 | 0 | 480 | 0 | YES | 1 | 0 | R&D
1097 | ID1097 | OSLH-F0 | 60 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
1098 | ID1098 | OSLH-F1 | 30 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1099 | ID1099 | OSLH-F2 | 30 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1100 | ID1100 | OSLH-F3 | 30 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1101 | ID1101 | OSLH-F4 | 30 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1102 | ID1102 | OSLH-F5 | 300 | 0 | 480 | 0 | YES | 1 | 0 | R&D
1103 | ID1103 | SSH in Liquid Floodback | 5 | 0 | 10 | 0 | YES | 1 | 0 | R&D
1104 | ID1104 | Time in Liquid Floodback | 60 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
1105 | ID1105 | EXV SH in Liquid Floodback | 6 Deg | 0 | 10 | 0 | YES | 1 | 0 | R&D
1106 | ID1106 | DSH A1 | 20 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1107 | ID1107 | DSH A2 | 5 | 0 | 30 | 0 | YES | 1 | 0 | R&D
1108 | ID1108 | DSH B1 | 30 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1109 | ID1109 | DSH B2 | 7 | 0 | 30 | 0 | YES | 1 | 0 | R&D
1110 | ID1110 | DSH C1 | 40 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1111 | ID1111 | DSH C2 | 9 | 0 | 30 | 0 | YES | 1 | 0 | R&D
1112 | ID1112 | DSH D1 | 50 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1113 | ID1113 | DSH D2 | 12 | 0 | 30 | 0 | YES | 1 | 0 | R&D
1114 | ID1114 | DSH E1 | 60 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1115 | ID1115 | DSH E2 | 14 | 0 | 30 | 0 | YES | 1 | 0 | R&D
1116 | ID1116 | DSH F1 | 70 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1117 | ID1117 | DSH F2 | 16 | 0 | 30 | 0 | YES | 1 | 0 | R&D
1118 | ID1118 | DSH G1 | 80 rps | 0 | 90 | 0 | YES | 1 | 0 | R&D
1119 | ID1119 | DSH G2 | 18 | 0 | 30 | 0 | YES | 1 | 0 | R&D
1120 | ID1120 | DSH H1 | 90 rps | 0 | 100 | 0 | YES | 1 | 0 | R&D
1121 | ID1121 | DSH H2 | 22 | 0 | 30 | 0 | YES | 1 | 0 | R&D
1122 | ID1122 | RPS in Ref Recovery | 50 rps | 0 | 100 | 0 | YES | 1 | 0 | R&D
1123 | ID1123 | LP in Ref Recovery | 120 psi | 0 | 300 | 0 | YES | 1 | 0 | R&D
1124 | ID1124 | LP time in Ref Recovery | 120 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
1125 | ID1125 | RTBC Tgt Liq Temp | 16 | -10 | 90 | 0 | YES | 1 | 0 | R&D
1126 | ID1126 | RTBC DSH | 20 | 0 | 30 | 0 | YES | 1 | 0 | R&D
1127 | ID1127 | RTBC Max RPS | 66 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1128 | ID1128 | RTBC I Fan | NC | LL | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1129 | ID1129 | RTBC O Fan | NC | 0 | 19 | 0 | YES | 1 | 0 | R&D
1130 | ID1130 | Max EXV SH_TGT | 7 | 0 | 20 | 0 | YES | 1 | 0 | R&D
1131 | ID1131 | RTC A1 | 16 | -10 | 30 | 0 | YES | 1 | 0 | R&D
1132 | ID1132 | RTC A2 | 12 | -10 | 30 | 0 | YES | 1 | 0 | R&D
1133 | ID1133 | RTC A3 | 9 | -10 | 30 | 0 | YES | 1 | 0 | R&D
1134 | ID1134 | RTC B1 | 16 | -10 | 30 | 0 | YES | 1 | 0 | R&D
1135 | ID1135 | RTC B2 | 12 | -10 | 30 | 0 | YES | 1 | 0 | R&D
1136 | ID1136 | RTC B3 | 9 | -10 | 30 | 0 | YES | 1 | 0 | R&D
1137 | ID1137 | RTC C1 | 13 | -10 | 30 | 0 | YES | 1 | 0 | R&D
1138 | ID1138 | RTC C2 | 9 | -10 | 30 | 0 | YES | 1 | 0 | R&D
1139 | ID1139 | RTC C3 | 6 | -10 | 30 | 0 | YES | 1 | 0 | R&D
1140 | ID1140 | Auto Gas HP Rate | 30 psi | 0 | 500 | 0 | YES | 1 | 0 | R&D
1141 | ID1141 | Auto Gas HP | 500 psi | 0 | 900 | 0 | YES | 1 | 0 | R&D
1142 | ID1142 | Auto Gas Preset A1 | 5 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1143 | ID1143 | Auto Gas Preset A2 | 10 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1144 | ID1144 | Auto Gas Preset A3 | 20 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1145 | ID1145 | Auto Gas Preset A4 | 25 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1146 | ID1146 | Auto Gas Preset A5 | 30 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1147 | ID1147 | Auto Gas Preset A6 | 35 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1148 | ID1148 | Auto Gas Preset A7 | 40 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1149 | ID1149 | Auto Gas Preset A8 | 45 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1150 | ID1150 | Auto Gas Preset A9 | 50 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1151 | ID1151 | Auto Gas Preset A10 | 55 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1152 | ID1152 | Auto Gas Preset B1 | 200 | 0 | 900 | 0 | YES | 1 | 0 | R&D
1153 | ID1153 | Auto Gas Preset B2 | 200 | 0 | 900 | 0 | YES | 1 | 0 | R&D
1154 | ID1154 | Auto Gas Preset B3 | 200 | 0 | 900 | 0 | YES | 1 | 0 | R&D
1155 | ID1155 | Auto Gas Preset B4 | 200 | 0 | 900 | 0 | YES | 1 | 0 | R&D
1156 | ID1156 | Auto Gas Preset B5 | 200 | 0 | 900 | 0 | YES | 1 | 0 | R&D
1157 | ID1157 | Auto Gas Preset B6 | 200 | 0 | 900 | 0 | YES | 1 | 0 | R&D
1158 | ID1158 | Auto Gas Preset B7 | 200 | 0 | 900 | 0 | YES | 1 | 0 | R&D
1159 | ID1159 | Auto Gas Preset B8 | 200 | 0 | 900 | 0 | YES | 1 | 0 | R&D
1160 | ID1160 | Auto Gas Preset B9 | 200 | 0 | 900 | 0 | YES | 1 | 0 | R&D
1161 | ID1161 | Auto Gas Preset B10 | 200 | 0 | 900 | 0 | YES | 1 | 0 | R&D
1162 | ID1162 | Auto Gas Preset C1 | 200 | 0 | 900 | 0 | YES | 1 | 0 | R&D
1163 | ID1163 | Auto Gas Preset C2 | 200 | 0 | 900 | 0 | YES | 1 | 0 | R&D
1164 | ID1164 | Auto Gas Preset C3 | 200 | 0 | 900 | 0 | YES | 1 | 0 | R&D
1165 | ID1165 | Auto Gas Preset C4 | 200 | 0 | 900 | 0 | YES | 1 | 0 | R&D
1166 | ID1166 | Auto Gas Preset C5 | 200 | 0 | 900 | 0 | YES | 1 | 0 | R&D
1167 | ID1167 | Auto Gas Preset C6 | 200 | 0 | 900 | 0 | YES | 1 | 0 | R&D
1168 | ID1168 | Auto Gas Preset C7 | 200 | 0 | 900 | 0 | YES | 1 | 0 | R&D
1169 | ID1169 | Auto Gas Preset C8 | 200 | 0 | 900 | 0 | YES | 1 | 0 | R&D
1170 | ID1170 | Auto Gas Preset C9 | 200 | 0 | 900 | 0 | YES | 1 | 0 | R&D
1171 | ID1171 | Auto Gas Preset C10 | 200 | 0 | 900 | 0 | YES | 1 | 0 | R&D
1172 | ID1172 | Auto Gas Preset % | 30 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1173 | ID1173 | Auto Gas EXV at Static | 100 | 0 | 3000 | 0 | YES | 1 | 0 | R&D
1174 | ID1174 | Auto Gas Comp RPS | 60 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1175 | ID1175 | Auto Gas ODU Fan | 12 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1176 | ID1176 | Auto GC Preset for SC A1 | 5 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1177 | ID1177 | Auto GC Preset for SC A2 | 10 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1178 | ID1178 | Auto GC Preset for SC A3 | 20 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1179 | ID1179 | Auto GC Preset for SC A4 | 25 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1180 | ID1180 | Auto GC Preset for SC A5 | 30 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1181 | ID1181 | Auto GC Preset for SC A6 | 35 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1182 | ID1182 | Auto GC Preset for SC A7 | 40 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1183 | ID1183 | Auto GC Preset for SC A8 | 45 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1184 | ID1184 | Auto GC Preset for SC A9 | 50 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1185 | ID1185 | Auto GC Preset for SC A10 | 55 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1186 | ID1186 | Auto GC Preset for SC B1 | 400 | 0 | 1000 | 0 | YES | 1 | 0 | R&D
1187 | ID1187 | Auto GC Preset for SC B2 | 410 | 0 | 1000 | 0 | YES | 1 | 0 | R&D
1188 | ID1188 | Auto GC Preset for SC B3 | 420 | 0 | 1000 | 0 | YES | 1 | 0 | R&D
1189 | ID1189 | Auto GC Preset for SC B4 | 430 | 0 | 1000 | 0 | YES | 1 | 0 | R&D
1190 | ID1190 | Auto GC Preset for SC B5 | 440 | 0 | 1000 | 0 | YES | 1 | 0 | R&D
1191 | ID1191 | Auto GC Preset for SC B6 | 450 | 0 | 1000 | 0 | YES | 1 | 0 | R&D
1192 | ID1192 | Auto GC Preset for SC B7 | 460 | 0 | 1000 | 0 | YES | 1 | 0 | R&D
1193 | ID1193 | Auto GC Preset for SC B8 | 470 | 0 | 1000 | 0 | YES | 1 | 0 | R&D
1194 | ID1194 | Auto GC Preset for SC B9 | 480 | 0 | 1000 | 0 | YES | 1 | 0 | R&D
1195 | ID1195 | Auto GC Preset for SC B10 | 490 | 0 | 1000 | 0 | YES | 1 | 0 | R&D
1196 | ID1196 | Auto GC Preset for SC C1 | 16 | 16 | 40 | 0 | YES | 1 | 0 | R&D
1197 | ID1197 | Auto GC Preset for SC C2 | 16 | 16 | 40 | 0 | YES | 1 | 0 | R&D
1198 | ID1198 | Auto GC Preset for SC C3 | 18 | 16 | 40 | 0 | YES | 1 | 0 | R&D
1199 | ID1199 | Auto GC Preset for SC C4 | 18 | 16 | 40 | 0 | YES | 1 | 0 | R&D
1200 | ID1200 | Auto GC Preset for SC C5 | 20 | 16 | 40 | 0 | YES | 1 | 0 | R&D
1201 | ID1201 | Auto GC Preset for SC C6 | 20 | 16 | 40 | 0 | YES | 1 | 0 | R&D
1202 | ID1202 | Auto GC Preset for SC C7 | 22 | 16 | 40 | 0 | YES | 1 | 0 | R&D
1203 | ID1203 | Auto GC Preset for SC C8 | 22 | 16 | 40 | 0 | YES | 1 | 0 | R&D
1204 | ID1204 | Auto GC Preset for SC C9 | 24 | 16 | 40 | 0 | YES | 1 | 0 | R&D
1205 | ID1205 | Auto GC Preset for SC C10 | 24 | 16 | 40 | 0 | YES | 1 | 0 | R&D
1206 | ID1206 | Auto GC Preset for SC D1 | 200 | 0 | 600 | 0 | YES | 1 | 0 | R&D
1207 | ID1207 | Auto GC Preset for SC D2 | 195 | 0 | 600 | 0 | YES | 1 | 0 | R&D
1208 | ID1208 | Auto GC Preset for SC D3 | 190 | 0 | 600 | 0 | YES | 1 | 0 | R&D
1209 | ID1209 | Auto GC Preset for SC D4 | 185 | 0 | 600 | 0 | YES | 1 | 0 | R&D
1210 | ID1210 | Auto GC Preset for SC D5 | 180 | 0 | 600 | 0 | YES | 1 | 0 | R&D
1211 | ID1211 | Auto GC Preset for SC D6 | 175 | 0 | 600 | 0 | YES | 1 | 0 | R&D
1212 | ID1212 | Auto GC Preset for SC D7 | 170 | 0 | 600 | 0 | YES | 1 | 0 | R&D
1213 | ID1213 | Auto GC Preset for SC D8 | 165 | 0 | 600 | 0 | YES | 1 | 0 | R&D
1214 | ID1214 | Auto GC Preset for SC D9 | 160 | 0 | 600 | 0 | YES | 1 | 0 | R&D
1215 | ID1215 | Auto GC Preset for SC D10 | 155 | 0 | 600 | 0 | YES | 1 | 0 | R&D
1216 | ID1216 | Auto GC Preset for SC E1 | 1 | 0 | 5 | 0 | YES | 0.1 | 0 | R&D
1217 | ID1217 | Auto GC Preset for SC E2 | 1 | 0 | 5 | 0 | YES | 0.1 | 0 | R&D
1218 | ID1218 | Auto GC Preset for SC E3 | 1 | 0 | 5 | 0 | YES | 0.1 | 0 | R&D
1219 | ID1219 | Auto GC Preset for SC E4 | 1 | 0 | 5 | 0 | YES | 0.1 | 0 | R&D
1220 | ID1220 | Auto GC Preset for SC E5 | 1 | 0 | 5 | 0 | YES | 0.1 | 0 | R&D
1221 | ID1221 | Auto GC Preset for SC E6 | 1 | 0 | 5 | 0 | YES | 0.1 | 0 | R&D
1222 | ID1222 | Auto GC Preset for SC E7 | 1 | 0 | 5 | 0 | YES | 0.1 | 0 | R&D
1223 | ID1223 | Auto GC Preset for SC E8 | 1 | 0 | 5 | 0 | YES | 0.1 | 0 | R&D
1224 | ID1224 | Auto GC Preset for SC E9 | 1 | 0 | 5 | 0 | YES | 0.1 | 0 | R&D
1225 | ID1225 | Auto GC Preset for SC E10 | 1 | 0 | 5 | 0 | YES | 0.1 | 0 | R&D
1226 | ID1226 | Auto GC Preset for SC F1 | 5 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1227 | ID1227 | Auto GC Preset for SC F2 | 10 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1228 | ID1228 | Auto GC Preset for SC F3 | 20 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1229 | ID1229 | Auto GC Preset for SC F4 | 25 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1230 | ID1230 | Auto GC Preset for SC F5 | 30 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1231 | ID1231 | Auto GC Preset for SC F6 | 35 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1232 | ID1232 | Auto GC Preset for SC F7 | 40 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1233 | ID1233 | Auto GC Preset for SC F8 | 45 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1234 | ID1234 | Auto GC Preset for SC F9 | 50 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1235 | ID1235 | Auto GC Preset for SC F10 | 55 | -40 | 60 | 0 | YES | 1 | 0 | R&D
1236 | ID1236 | Auto GC Preset for SC G1 | 400 | 0 | 1000 | 0 | YES | 1 | 0 | R&D
1237 | ID1237 | Auto GC Preset for SC G2 | 410 | 0 | 1000 | 0 | YES | 1 | 0 | R&D
1238 | ID1238 | Auto GC Preset for SC G3 | 420 | 0 | 1000 | 0 | YES | 1 | 0 | R&D
1239 | ID1239 | Auto GC Preset for SC G4 | 430 | 0 | 1000 | 0 | YES | 1 | 0 | R&D
1240 | ID1240 | Auto GC Preset for SC G5 | 440 | 0 | 1000 | 0 | YES | 1 | 0 | R&D
1241 | ID1241 | Auto GC Preset for SC G6 | 450 | 0 | 1000 | 0 | YES | 1 | 0 | R&D
1242 | ID1242 | Auto GC Preset for SC G7 | 460 | 0 | 1000 | 0 | YES | 1 | 0 | R&D
1243 | ID1243 | Auto GC Preset for SC G8 | 470 | 0 | 1000 | 0 | YES | 1 | 0 | R&D
1244 | ID1244 | Auto GC Preset for SC G9 | 480 | 0 | 1000 | 0 | YES | 1 | 0 | R&D
1245 | ID1245 | Auto GC Preset for SC G10 | 490 | 0 | 1000 | 0 | YES | 1 | 0 | R&D
1246 | ID1246 | Auto GC Preset for SC H1 | 16 | 16 | 40 | 0 | YES | 1 | 0 | R&D
1247 | ID1247 | Auto GC Preset for SC H2 | 16 | 16 | 40 | 0 | YES | 1 | 0 | R&D
1248 | ID1248 | Auto GC Preset for SC H3 | 18 | 16 | 40 | 0 | YES | 1 | 0 | R&D
1249 | ID1249 | Auto GC Preset for SC H4 | 18 | 16 | 40 | 0 | YES | 1 | 0 | R&D
1250 | ID1250 | Auto GC Preset for SC H5 | 20 | 16 | 40 | 0 | YES | 1 | 0 | R&D
1251 | ID1251 | Auto GC Preset for SC H6 | 20 | 16 | 40 | 0 | YES | 1 | 0 | R&D
1252 | ID1252 | Auto GC Preset for SC H7 | 22 | 16 | 40 | 0 | YES | 1 | 0 | R&D
1253 | ID1253 | Auto GC Preset for SC H8 | 22 | 16 | 40 | 0 | YES | 1 | 0 | R&D
1254 | ID1254 | Auto GC Preset for SC H9 | 24 | 16 | 40 | 0 | YES | 1 | 0 | R&D
1255 | ID1255 | Auto GC Preset for SC H10 | 24 | 16 | 40 | 0 | YES | 1 | 0 | R&D
1256 | ID1256 | Auto GC Preset for SC I1 | 200 | 0 | 600 | 0 | YES | 1 | 0 | R&D
1257 | ID1257 | Auto GC Preset for SC I2 | 195 | 0 | 600 | 0 | YES | 1 | 0 | R&D
1258 | ID1258 | Auto GC Preset for SC I3 | 190 | 0 | 600 | 0 | YES | 1 | 0 | R&D
1259 | ID1259 | Auto GC Preset for SC I4 | 185 | 0 | 600 | 0 | YES | 1 | 0 | R&D
1260 | ID1260 | Auto GC Preset for SC I5 | 180 | 0 | 600 | 0 | YES | 1 | 0 | R&D
1261 | ID1261 | Auto GC Preset for SC I6 | 175 | 0 | 600 | 0 | YES | 1 | 0 | R&D
1262 | ID1262 | Auto GC Preset for SC I7 | 170 | 0 | 600 | 0 | YES | 1 | 0 | R&D
1263 | ID1263 | Auto GC Preset for SC I8 | 165 | 0 | 600 | 0 | YES | 1 | 0 | R&D
1264 | ID1264 | Auto GC Preset for SC I9 | 160 | 0 | 600 | 0 | YES | 1 | 0 | R&D
1265 | ID1265 | Auto GC Preset for SC I10 | 155 | 0 | 600 | 0 | YES | 1 | 0 | R&D
1266 | ID1266 | Auto GC Preset for SC J1 | 3 | 0 | 5 | 0 | YES | 0.1 | 0 | R&D
1267 | ID1267 | Auto GC Preset for SC J2 | 3 | 0 | 5 | 0 | YES | 0.1 | 0 | R&D
1268 | ID1268 | Auto GC Preset for SC J3 | 3 | 0 | 5 | 0 | YES | 0.1 | 0 | R&D
1269 | ID1269 | Auto GC Preset for SC J4 | 3 | 0 | 5 | 0 | YES | 0.1 | 0 | R&D
1270 | ID1270 | Auto GC Preset for SC J5 | 3 | 0 | 5 | 0 | YES | 0.1 | 0 | R&D
1271 | ID1271 | Auto GC Preset for SC J6 | 3 | 0 | 5 | 0 | YES | 0.1 | 0 | R&D
1272 | ID1272 | Auto GC Preset for SC J7 | 3 | 0 | 5 | 0 | YES | 0.1 | 0 | R&D
1273 | ID1273 | Auto GC Preset for SC J8 | 3 | 0 | 5 | 0 | YES | 0.1 | 0 | R&D
1274 | ID1274 | Auto GC Preset for SC J9 | 3 | 0 | 5 | 0 | YES | 0.1 | 0 | R&D
1275 | ID1275 | Auto GC Preset for SC J10 | 3 | 0 | 5 | 0 | YES | 0.1 | 0 | R&D
1276 | ID1276 | Auto GC Diversity 1 | 0.8 | 0 | 3 | 0 | YES | 0.1 | 0 | R&D
1277 | ID1277 | Auto GC Diversity 2 | 0.9 | 0 | 3 | 0 | YES | 0.1 | 0 | R&D
1278 | ID1278 | Auto GC Diversity 3 | 1 | 0 | 3 | 0 | YES | 0.1 | 0 | R&D
1279 | ID1279 | Auto GC Diversity 4 | 1.1 | 0 | 3 | 0 | YES | 0.1 | 0 | R&D
1280 | ID1280 | Auto GC Diversity 5 | 1.2 | 0 | 3 | 0 | YES | 0.1 | 0 | R&D
1281 | ID1281 | Auto GC Diversity 6 | 1.3 | 0 | 3 | 0 | YES | 0.1 | 0 | R&D
1282 | ID1282 | Auto Gas EXV at Running | 200 | 0 | 480 | 0 | YES | 1 | 0 | R&D
1283 | ID1283 | Auto Gas EXV Delta SC 1 | 80 | 0 | 480 | 0 | YES | 1 | 0 | R&D
1284 | ID1284 | Auto Gas EXV Delta SC 2 | 120 | 0 | 480 | 0 | YES | 1 | 0 | R&D
1285 | ID1285 | Auto Gas EXV Delta SC 3 | 150 | 0 | 480 | 0 | YES | 1 | 0 | R&D
1286 | ID1286 | Liq Inj Step 1 EXV | 70 | 0 | 480 | 0 | YES | 1 | 0 | R&D
1287 | ID1287 | Liq Inj Step 2 EXV | 90 | 0 | 480 | 0 | YES | 1 | 0 | R&D
1288 | ID1288 | Silent Mode A1 | Me | 0 | 19 | 0 | YES | 1 | 0 | R&D
1289 | ID1289 | Silent Mode A2 | Me | 0 | 19 | 0 | YES | 1 | 0 | R&D
1290 | ID1290 | Silent Mode A3 | Me | 0 | 19 | 0 | YES | 1 | 0 | R&D
1291 | ID1291 | Silent Mode A4 | Me | 0 | 19 | 0 | YES | 1 | 0 | R&D
1292 | ID1292 | Silent Mode B1 | -6 | 0 | -50 | 0 | YES | 1 | 0 | R&D
1293 | ID1293 | Silent Mode B2 | -3 | 0 | -50 | 0 | YES | 1 | 0 | R&D
1294 | ID1294 | Silent Mode B3 | -6 | 0 | -50 | 0 | YES | 1 | 0 | R&D
1295 | ID1295 | Silent Mode B4 | -3 | 0 | -50 | 0 | YES | 1 | 0 | R&D
1296 | ID1296 | Silent Mode Max TOC 1 | 9.8 | 0 | 150 | 0 | YES | 0.1 | 0 | R&D
1297 | ID1297 | Silent Mode Max TOC 2 | 11.2 | 0 | 150 | 0 | YES | 0.1 | 0 | R&D
1298 | ID1298 | Silent Mode Max TOC 3 | 14 | 0 | 150 | 0 | YES | 0.1 | 0 | R&D
1299 | ID1299 | Silent Mode Max TOC 4 | 16.8 | 0 | 150 | 0 | YES | 0.1 | 0 | R&D
1300 | ID1300 | Silent Mode Max TOC 5 | 19.6 | 0 | 150 | 0 | YES | 0.1 | 0 | R&D
1301 | ID1301 | Silent Mode Max TOC 6 | 22.4 | 0 | 150 | 0 | YES | 0.1 | 0 | R&D
1302 | ID1302 | Silent Mode Max TOC 7 | 25.2 | 0 | 150 | 0 | YES | 0.1 | 0 | R&D
1303 | ID1303 | Silent Mode Max TOC 8 | 28 | 0 | 150 | 0 | YES | 0.1 | 0 | R&D
1304 | ID1304 | Silent Mode Max TOC 9 | 30.8 | 0 | 150 | 0 | YES | 0.1 | 0 | R&D
1305 | ID1305 | Silent Mode Max TOC 10 | 33.6 | 0 | 150 | 0 | YES | 0.1 | 0 | R&D
1306 | ID1306 | Silent Mode Max TOC 11 | 36.4 | 0 | 150 | 0 | YES | 0.1 | 0 | R&D
1307 | ID1307 | Silent Mode Max TOC 12 | 39.2 | 0 | 150 | 0 | YES | 0.1 | 0 | R&D
1308 | ID1308 | Silent Mode Max TOC 13 | 39.2 | 0 | 150 | 0 | YES | 0.1 | 0 | R&D
1309 | ID1309 | Silent Mode Max TOC 14 | 39.2 | 0 | 150 | 0 | YES | 0.1 | 0 | R&D
1310 | ID1310 | Silent Mode Max TOC 15 | 39.2 | 0 | 150 | 0 | YES | 0.1 | 0 | R&D
1311 | ID1311 | Performance A1 | 58 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1312 | ID1312 | Performance A2 | 58 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1313 | ID1313 | Performance A3 | Low | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1314 | ID1314 | Performance A4 | 1 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1315 | ID1315 | Performance A5 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1316 | ID1316 | Performance A6 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1317 | ID1317 | Performance A7 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1318 | ID1318 | Performance A8 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1319 | ID1319 | Performance A9 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1320 | ID1320 | Performance A10 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1321 | ID1321 | Performance A11 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1322 | ID1322 | Performance A12 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1323 | ID1323 | Performance A13 | 65 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1324 | ID1324 | Performance A14 | 65 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1325 | ID1325 | Performance A15 | Low | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1326 | ID1326 | Performance A16 | 2 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1327 | ID1327 | Performance A17 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1328 | ID1328 | Performance A18 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1329 | ID1329 | Performance A19 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1330 | ID1330 | Performance A20 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1331 | ID1331 | Performance A21 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1332 | ID1332 | Performance A22 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1333 | ID1333 | Performance A23 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1334 | ID1334 | Performance A24 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1335 | ID1335 | Performance A25 | 65 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1336 | ID1336 | Performance A26 | 65 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1337 | ID1337 | Performance A27 | Low | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1338 | ID1338 | Performance A28 | 2 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1339 | ID1339 | Performance A29 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1340 | ID1340 | Performance A30 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1341 | ID1341 | Performance A31 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1342 | ID1342 | Performance A32 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1343 | ID1343 | Performance A33 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1344 | ID1344 | Performance A34 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1345 | ID1345 | Performance A35 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1346 | ID1346 | Performance A36 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1347 | ID1347 | Performance A37 | 65 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1348 | ID1348 | Performance A38 | 65 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1349 | ID1349 | Performance A39 | Low | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1350 | ID1350 | Performance A40 | 2 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1351 | ID1351 | Performance A41 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1352 | ID1352 | Performance A42 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1353 | ID1353 | Performance A43 | ON | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1354 | ID1354 | Performance A44 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1355 | ID1355 | Performance A45 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1356 | ID1356 | Performance A46 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1357 | ID1357 | Performance A47 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1358 | ID1358 | Performance A48 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1359 | ID1359 | Performance B1 | 66 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1360 | ID1360 | Performance B2 | 66 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1361 | ID1361 | Performance B3 | Me | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1362 | ID1362 | Performance B4 | 1 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1363 | ID1363 | Performance B5 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1364 | ID1364 | Performance B6 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1365 | ID1365 | Performance B7 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1366 | ID1366 | Performance B8 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1367 | ID1367 | Performance B9 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1368 | ID1368 | Performance B10 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1369 | ID1369 | Performance B11 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1370 | ID1370 | Performance B12 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1371 | ID1371 | Performance B13 | 74 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1372 | ID1372 | Performance B14 | 74 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1373 | ID1373 | Performance B15 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1374 | ID1374 | Performance B16 | 1 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1375 | ID1375 | Performance B17 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1376 | ID1376 | Performance B18 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1377 | ID1377 | Performance B19 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1378 | ID1378 | Performance B20 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1379 | ID1379 | Performance B21 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1380 | ID1380 | Performance B22 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1381 | ID1381 | Performance B23 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1382 | ID1382 | Performance B24 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1383 | ID1383 | Performance B25 | 74 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1384 | ID1384 | Performance B26 | 74 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1385 | ID1385 | Performance B27 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1386 | ID1386 | Performance B28 | 1 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1387 | ID1387 | Performance B29 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1388 | ID1388 | Performance B30 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1389 | ID1389 | Performance B31 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1390 | ID1390 | Performance B32 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1391 | ID1391 | Performance B33 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1392 | ID1392 | Performance B34 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1393 | ID1393 | Performance B35 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1394 | ID1394 | Performance B36 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1395 | ID1395 | Performance B37 | 74 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1396 | ID1396 | Performance B38 | 74 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1397 | ID1397 | Performance B39 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1398 | ID1398 | Performance B40 | 1 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1399 | ID1399 | Performance B41 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1400 | ID1400 | Performance B42 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1401 | ID1401 | Performance B43 | ON | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1402 | ID1402 | Performance B44 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1403 | ID1403 | Performance B45 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1404 | ID1404 | Performance B46 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1405 | ID1405 | Performance B47 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1406 | ID1406 | Performance B48 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1407 | ID1407 | Performance C1 | 57 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1408 | ID1408 | Performance C2 | 42 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1409 | ID1409 | Performance C3 | Me | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1410 | ID1410 | Performance C4 | 6 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1411 | ID1411 | Performance C5 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1412 | ID1412 | Performance C6 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1413 | ID1413 | Performance C7 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1414 | ID1414 | Performance C8 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1415 | ID1415 | Performance C9 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1416 | ID1416 | Performance C10 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1417 | ID1417 | Performance C11 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1418 | ID1418 | Performance C12 | 11 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1419 | ID1419 | Performance C13 | 63 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1420 | ID1420 | Performance C14 | 50 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1421 | ID1421 | Performance C15 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1422 | ID1422 | Performance C16 | 4 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1423 | ID1423 | Performance C17 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1424 | ID1424 | Performance C18 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1425 | ID1425 | Performance C19 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1426 | ID1426 | Performance C20 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1427 | ID1427 | Performance C21 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1428 | ID1428 | Performance C22 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1429 | ID1429 | Performance C23 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1430 | ID1430 | Performance C24 | 11 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1431 | ID1431 | Performance C25 | 63 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1432 | ID1432 | Performance C26 | 50 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1433 | ID1433 | Performance C27 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1434 | ID1434 | Performance C28 | 4 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1435 | ID1435 | Performance C29 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1436 | ID1436 | Performance C30 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1437 | ID1437 | Performance C31 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1438 | ID1438 | Performance C32 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1439 | ID1439 | Performance C33 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1440 | ID1440 | Performance C34 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1441 | ID1441 | Performance C35 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1442 | ID1442 | Performance C36 | 11 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1443 | ID1443 | Performance C37 | 63 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1444 | ID1444 | Performance C38 | 50 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1445 | ID1445 | Performance C39 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1446 | ID1446 | Performance C40 | 4 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1447 | ID1447 | Performance C41 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1448 | ID1448 | Performance C42 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1449 | ID1449 | Performance C43 | ON | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1450 | ID1450 | Performance C44 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1451 | ID1451 | Performance C45 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1452 | ID1452 | Performance C46 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1453 | ID1453 | Performance C47 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1454 | ID1454 | Performance C48 | 11 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1455 | ID1455 | Performance D1 | 48 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1456 | ID1456 | Performance D2 | 48 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1457 | ID1457 | Performance D3 | Me | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1458 | ID1458 | Performance D4 | 2 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1459 | ID1459 | Performance D5 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1460 | ID1460 | Performance D6 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1461 | ID1461 | Performance D7 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1462 | ID1462 | Performance D8 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1463 | ID1463 | Performance D9 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1464 | ID1464 | Performance D10 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1465 | ID1465 | Performance D11 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1466 | ID1466 | Performance D12 | 8 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1467 | ID1467 | Performance D13 | 54 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1468 | ID1468 | Performance D14 | 54 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1469 | ID1469 | Performance D15 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1470 | ID1470 | Performance D16 | 3 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1471 | ID1471 | Performance D17 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1472 | ID1472 | Performance D18 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1473 | ID1473 | Performance D19 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1474 | ID1474 | Performance D20 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1475 | ID1475 | Performance D21 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1476 | ID1476 | Performance D22 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1477 | ID1477 | Performance D23 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1478 | ID1478 | Performance D24 | 9 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1479 | ID1479 | Performance D25 | 54 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1480 | ID1480 | Performance D26 | 54 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1481 | ID1481 | Performance D27 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1482 | ID1482 | Performance D28 | 3 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1483 | ID1483 | Performance D29 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1484 | ID1484 | Performance D30 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1485 | ID1485 | Performance D31 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1486 | ID1486 | Performance D32 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1487 | ID1487 | Performance D33 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1488 | ID1488 | Performance D34 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1489 | ID1489 | Performance D35 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1490 | ID1490 | Performance D36 | 9 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1491 | ID1491 | Performance D37 | 54 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1492 | ID1492 | Performance D38 | 54 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1493 | ID1493 | Performance D39 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1494 | ID1494 | Performance D40 | 3 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1495 | ID1495 | Performance D41 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1496 | ID1496 | Performance D42 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1497 | ID1497 | Performance D43 | ON | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1498 | ID1498 | Performance D44 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1499 | ID1499 | Performance D45 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1500 | ID1500 | Performance D46 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1501 | ID1501 | Performance D47 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1502 | ID1502 | Performance D48 | 9 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1503 | ID1503 | Performance E1 | 54 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1504 | ID1504 | Performance E2 | 54 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1505 | ID1505 | Performance E3 | Me | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1506 | ID1506 | Performance E4 | 3 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1507 | ID1507 | Performance E5 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1508 | ID1508 | Performance E6 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1509 | ID1509 | Performance E7 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1510 | ID1510 | Performance E8 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1511 | ID1511 | Performance E9 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1512 | ID1512 | Performance E10 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1513 | ID1513 | Performance E11 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1514 | ID1514 | Performance E12 | 9 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1515 | ID1515 | Performance E13 | 57 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1516 | ID1516 | Performance E14 | 57 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1517 | ID1517 | Performance E15 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1518 | ID1518 | Performance E16 | 4 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1519 | ID1519 | Performance E17 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1520 | ID1520 | Performance E18 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1521 | ID1521 | Performance E19 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1522 | ID1522 | Performance E20 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1523 | ID1523 | Performance E21 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1524 | ID1524 | Performance E22 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1525 | ID1525 | Performance E23 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1526 | ID1526 | Performance E24 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1527 | ID1527 | Performance E25 | 57 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1528 | ID1528 | Performance E26 | 57 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1529 | ID1529 | Performance E27 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1530 | ID1530 | Performance E28 | 4 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1531 | ID1531 | Performance E29 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1532 | ID1532 | Performance E30 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1533 | ID1533 | Performance E31 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1534 | ID1534 | Performance E32 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1535 | ID1535 | Performance E33 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1536 | ID1536 | Performance E34 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1537 | ID1537 | Performance E35 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1538 | ID1538 | Performance E36 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1539 | ID1539 | Performance E37 | 57 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1540 | ID1540 | Performance E38 | 57 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1541 | ID1541 | Performance E39 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1542 | ID1542 | Performance E40 | 4 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1543 | ID1543 | Performance E41 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1544 | ID1544 | Performance E42 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1545 | ID1545 | Performance E43 | ON | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1546 | ID1546 | Performance E44 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1547 | ID1547 | Performance E45 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1548 | ID1548 | Performance E46 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1549 | ID1549 | Performance E47 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1550 | ID1550 | Performance E48 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1551 | ID1551 | Performance F1 | 58 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1552 | ID1552 | Performance F2 | 58 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1553 | ID1553 | Performance F3 | Me | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1554 | ID1554 | Performance F4 | 6 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1555 | ID1555 | Performance F5 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1556 | ID1556 | Performance F6 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1557 | ID1557 | Performance F7 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1558 | ID1558 | Performance F8 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1559 | ID1559 | Performance F9 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1560 | ID1560 | Performance F10 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1561 | ID1561 | Performance F11 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1562 | ID1562 | Performance F12 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1563 | ID1563 | Performance F13 | 59 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1564 | ID1564 | Performance F14 | 59 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1565 | ID1565 | Performance F15 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1566 | ID1566 | Performance F16 | 3 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1567 | ID1567 | Performance F17 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1568 | ID1568 | Performance F18 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1569 | ID1569 | Performance F19 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1570 | ID1570 | Performance F20 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1571 | ID1571 | Performance F21 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1572 | ID1572 | Performance F22 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1573 | ID1573 | Performance F23 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1574 | ID1574 | Performance F24 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1575 | ID1575 | Performance F25 | 59 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1576 | ID1576 | Performance F26 | 59 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1577 | ID1577 | Performance F27 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1578 | ID1578 | Performance F28 | 3 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1579 | ID1579 | Performance F29 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1580 | ID1580 | Performance F30 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1581 | ID1581 | Performance F31 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1582 | ID1582 | Performance F32 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1583 | ID1583 | Performance F33 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1584 | ID1584 | Performance F34 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1585 | ID1585 | Performance F35 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1586 | ID1586 | Performance F36 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1587 | ID1587 | Performance F37 | 59 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1588 | ID1588 | Performance F38 | 59 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1589 | ID1589 | Performance F39 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1590 | ID1590 | Performance F40 | 3 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1591 | ID1591 | Performance F41 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1592 | ID1592 | Performance F42 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1593 | ID1593 | Performance F43 | ON | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1594 | ID1594 | Performance F44 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1595 | ID1595 | Performance F45 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1596 | ID1596 | Performance F46 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1597 | ID1597 | Performance F47 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1598 | ID1598 | Performance F48 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1599 | ID1599 | Performance G1 | 66 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1600 | ID1600 | Performance G2 | 65 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1601 | ID1601 | Performance G3 | Me | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1602 | ID1602 | Performance G4 | 3 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1603 | ID1603 | Performance G5 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1604 | ID1604 | Performance G6 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1605 | ID1605 | Performance G7 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1606 | ID1606 | Performance G8 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1607 | ID1607 | Performance G9 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1608 | ID1608 | Performance G10 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1609 | ID1609 | Performance G11 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1610 | ID1610 | Performance G12 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1611 | ID1611 | Performance G13 | 63 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1612 | ID1612 | Performance G14 | 63 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1613 | ID1613 | Performance G15 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1614 | ID1614 | Performance G16 | 4 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1615 | ID1615 | Performance G17 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1616 | ID1616 | Performance G18 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1617 | ID1617 | Performance G19 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1618 | ID1618 | Performance G20 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1619 | ID1619 | Performance G21 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1620 | ID1620 | Performance G22 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1621 | ID1621 | Performance G23 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1622 | ID1622 | Performance G24 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1623 | ID1623 | Performance G25 | 63 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1624 | ID1624 | Performance G26 | 63 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1625 | ID1625 | Performance G27 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1626 | ID1626 | Performance G28 | 4 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1627 | ID1627 | Performance G29 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1628 | ID1628 | Performance G30 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1629 | ID1629 | Performance G31 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1630 | ID1630 | Performance G32 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1631 | ID1631 | Performance G33 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1632 | ID1632 | Performance G34 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1633 | ID1633 | Performance G35 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1634 | ID1634 | Performance G36 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1635 | ID1635 | Performance G37 | 63 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1636 | ID1636 | Performance G38 | 63 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1637 | ID1637 | Performance G39 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1638 | ID1638 | Performance G40 | 4 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1639 | ID1639 | Performance G41 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1640 | ID1640 | Performance G42 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1641 | ID1641 | Performance G43 | ON | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1642 | ID1642 | Performance G44 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1643 | ID1643 | Performance G45 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1644 | ID1644 | Performance G46 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1645 | ID1645 | Performance G47 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1646 | ID1646 | Performance G48 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1647 | ID1647 | Performance H1 | 58 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1648 | ID1648 | Performance H2 | 59 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1649 | ID1649 | Performance H3 | Me | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1650 | ID1650 | Performance H4 | 0 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1651 | ID1651 | Performance H5 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1652 | ID1652 | Performance H6 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1653 | ID1653 | Performance H7 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1654 | ID1654 | Performance H8 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1655 | ID1655 | Performance H9 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1656 | ID1656 | Performance H10 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1657 | ID1657 | Performance H11 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1658 | ID1658 | Performance H12 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1659 | ID1659 | Performance H13 | 59 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1660 | ID1660 | Performance H14 | 60 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1661 | ID1661 | Performance H15 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1662 | ID1662 | Performance H16 | 5 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1663 | ID1663 | Performance H17 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1664 | ID1664 | Performance H18 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1665 | ID1665 | Performance H19 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1666 | ID1666 | Performance H20 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1667 | ID1667 | Performance H21 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1668 | ID1668 | Performance H22 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1669 | ID1669 | Performance H23 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1670 | ID1670 | Performance H24 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1671 | ID1671 | Performance H25 | 59 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1672 | ID1672 | Performance H26 | 60 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1673 | ID1673 | Performance H27 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1674 | ID1674 | Performance H28 | 5 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1675 | ID1675 | Performance H29 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1676 | ID1676 | Performance H30 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1677 | ID1677 | Performance H31 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1678 | ID1678 | Performance H32 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1679 | ID1679 | Performance H33 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1680 | ID1680 | Performance H34 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1681 | ID1681 | Performance H35 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1682 | ID1682 | Performance H36 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1683 | ID1683 | Performance H37 | 59 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1684 | ID1684 | Performance H38 | 60 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1685 | ID1685 | Performance H39 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1686 | ID1686 | Performance H40 | 5 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1687 | ID1687 | Performance H41 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1688 | ID1688 | Performance H42 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1689 | ID1689 | Performance H43 | ON | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1690 | ID1690 | Performance H44 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1691 | ID1691 | Performance H45 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1692 | ID1692 | Performance H46 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1693 | ID1693 | Performance H47 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1694 | ID1694 | Performance H48 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1695 | ID1695 | Performance I1 | 66 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1696 | ID1696 | Performance I2 | 66 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1697 | ID1697 | Performance I3 | Me | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1698 | ID1698 | Performance I4 | -3 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1699 | ID1699 | Performance I5 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1700 | ID1700 | Performance I6 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1701 | ID1701 | Performance I7 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1702 | ID1702 | Performance I8 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1703 | ID1703 | Performance I9 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1704 | ID1704 | Performance I10 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1705 | ID1705 | Performance I11 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1706 | ID1706 | Performance I12 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1707 | ID1707 | Performance I13 | 63 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1708 | ID1708 | Performance I14 | 63 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1709 | ID1709 | Performance I15 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1710 | ID1710 | Performance I16 | 6 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1711 | ID1711 | Performance I17 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1712 | ID1712 | Performance I18 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1713 | ID1713 | Performance I19 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1714 | ID1714 | Performance I20 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1715 | ID1715 | Performance I21 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1716 | ID1716 | Performance I22 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1717 | ID1717 | Performance I23 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1718 | ID1718 | Performance I24 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1719 | ID1719 | Performance I25 | 63 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1720 | ID1720 | Performance I26 | 63 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1721 | ID1721 | Performance I27 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1722 | ID1722 | Performance I28 | 6 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1723 | ID1723 | Performance I29 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1724 | ID1724 | Performance I30 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1725 | ID1725 | Performance I31 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1726 | ID1726 | Performance I32 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1727 | ID1727 | Performance I33 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1728 | ID1728 | Performance I34 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1729 | ID1729 | Performance I35 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1730 | ID1730 | Performance I36 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1731 | ID1731 | Performance I37 | 63 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1732 | ID1732 | Performance I38 | 63 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1733 | ID1733 | Performance I39 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1734 | ID1734 | Performance I40 | 6 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1735 | ID1735 | Performance I41 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1736 | ID1736 | Performance I42 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1737 | ID1737 | Performance I43 | ON | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1738 | ID1738 | Performance I44 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1739 | ID1739 | Performance I45 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1740 | ID1740 | Performance I46 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1741 | ID1741 | Performance I47 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1742 | ID1742 | Performance I48 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1743 | ID1743 | Performance J1 | 58 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1744 | ID1744 | Performance J2 | 60 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1745 | ID1745 | Performance J3 | Me | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1746 | ID1746 | Performance J4 | -6 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1747 | ID1747 | Performance J5 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1748 | ID1748 | Performance J6 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1749 | ID1749 | Performance J7 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1750 | ID1750 | Performance J8 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1751 | ID1751 | Performance J9 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1752 | ID1752 | Performance J10 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1753 | ID1753 | Performance J11 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1754 | ID1754 | Performance J12 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1755 | ID1755 | Performance J13 | 59 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1756 | ID1756 | Performance J14 | 61 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1757 | ID1757 | Performance J15 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1758 | ID1758 | Performance J16 | 7 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1759 | ID1759 | Performance J17 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1760 | ID1760 | Performance J18 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1761 | ID1761 | Performance J19 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1762 | ID1762 | Performance J20 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1763 | ID1763 | Performance J21 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1764 | ID1764 | Performance J22 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1765 | ID1765 | Performance J23 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1766 | ID1766 | Performance J24 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1767 | ID1767 | Performance J25 | 59 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1768 | ID1768 | Performance J26 | 61 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1769 | ID1769 | Performance J27 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1770 | ID1770 | Performance J28 | 7 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1771 | ID1771 | Performance J29 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1772 | ID1772 | Performance J30 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1773 | ID1773 | Performance J31 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1774 | ID1774 | Performance J32 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1775 | ID1775 | Performance J33 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1776 | ID1776 | Performance J34 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1777 | ID1777 | Performance J35 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1778 | ID1778 | Performance J36 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1779 | ID1779 | Performance J37 | 59 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1780 | ID1780 | Performance J38 | 61 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1781 | ID1781 | Performance J39 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1782 | ID1782 | Performance J40 | 7 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1783 | ID1783 | Performance J41 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1784 | ID1784 | Performance J42 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1785 | ID1785 | Performance J43 | ON | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1786 | ID1786 | Performance J44 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1787 | ID1787 | Performance J45 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1788 | ID1788 | Performance J46 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1789 | ID1789 | Performance J47 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1790 | ID1790 | Performance J48 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1791 | ID1791 | Performance K1 | 66 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1792 | ID1792 | Performance K2 | 67 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1793 | ID1793 | Performance K3 | Me | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1794 | ID1794 | Performance K4 | -9 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1795 | ID1795 | Performance K5 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1796 | ID1796 | Performance K6 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1797 | ID1797 | Performance K7 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1798 | ID1798 | Performance K8 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1799 | ID1799 | Performance K9 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1800 | ID1800 | Performance K10 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1801 | ID1801 | Performance K11 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1802 | ID1802 | Performance K12 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1803 | ID1803 | Performance K13 | 63 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1804 | ID1804 | Performance K14 | 65 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1805 | ID1805 | Performance K15 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1806 | ID1806 | Performance K16 | 8 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1807 | ID1807 | Performance K17 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1808 | ID1808 | Performance K18 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1809 | ID1809 | Performance K19 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1810 | ID1810 | Performance K20 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1811 | ID1811 | Performance K21 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1812 | ID1812 | Performance K22 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1813 | ID1813 | Performance K23 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1814 | ID1814 | Performance K24 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1815 | ID1815 | Performance K25 | 63 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1816 | ID1816 | Performance K26 | 65 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1817 | ID1817 | Performance K27 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1818 | ID1818 | Performance K28 | 8 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1819 | ID1819 | Performance K29 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1820 | ID1820 | Performance K30 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1821 | ID1821 | Performance K31 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1822 | ID1822 | Performance K32 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1823 | ID1823 | Performance K33 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1824 | ID1824 | Performance K34 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1825 | ID1825 | Performance K35 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1826 | ID1826 | Performance K36 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1827 | ID1827 | Performance K37 | 63 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1828 | ID1828 | Performance K38 | 65 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1829 | ID1829 | Performance K39 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1830 | ID1830 | Performance K40 | 8 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1831 | ID1831 | Performance K41 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1832 | ID1832 | Performance K42 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1833 | ID1833 | Performance K43 | ON | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1834 | ID1834 | Performance K44 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1835 | ID1835 | Performance K45 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1836 | ID1836 | Performance K46 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1837 | ID1837 | Performance K47 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1838 | ID1838 | Performance K48 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1839 | ID1839 | Performance L1 | 58 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1840 | ID1840 | Performance L2 | 61 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1841 | ID1841 | Performance L3 | Me | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1842 | ID1842 | Performance L4 | -12 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1843 | ID1843 | Performance L5 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1844 | ID1844 | Performance L6 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1845 | ID1845 | Performance L7 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1846 | ID1846 | Performance L8 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1847 | ID1847 | Performance L9 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1848 | ID1848 | Performance L10 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1849 | ID1849 | Performance L11 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1850 | ID1850 | Performance L12 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1851 | ID1851 | Performance L13 | 59 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1852 | ID1852 | Performance L14 | 62 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1853 | ID1853 | Performance L15 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1854 | ID1854 | Performance L16 | 9 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1855 | ID1855 | Performance L17 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1856 | ID1856 | Performance L18 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1857 | ID1857 | Performance L19 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1858 | ID1858 | Performance L20 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1859 | ID1859 | Performance L21 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1860 | ID1860 | Performance L22 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1861 | ID1861 | Performance L23 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1862 | ID1862 | Performance L24 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1863 | ID1863 | Performance L25 | 59 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1864 | ID1864 | Performance L26 | 62 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1865 | ID1865 | Performance L27 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1866 | ID1866 | Performance L28 | 9 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1867 | ID1867 | Performance L29 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1868 | ID1868 | Performance L30 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1869 | ID1869 | Performance L31 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1870 | ID1870 | Performance L32 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1871 | ID1871 | Performance L33 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1872 | ID1872 | Performance L34 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1873 | ID1873 | Performance L35 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1874 | ID1874 | Performance L36 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1875 | ID1875 | Performance L37 | 59 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1876 | ID1876 | Performance L38 | 62 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1877 | ID1877 | Performance L39 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1878 | ID1878 | Performance L40 | 9 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1879 | ID1879 | Performance L41 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1880 | ID1880 | Performance L42 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1881 | ID1881 | Performance L43 | ON | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1882 | ID1882 | Performance L44 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1883 | ID1883 | Performance L45 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1884 | ID1884 | Performance L46 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1885 | ID1885 | Performance L47 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1886 | ID1886 | Performance L48 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1887 | ID1887 | Performance M1 | 66 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1888 | ID1888 | Performance M2 | 68 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1889 | ID1889 | Performance M3 | Me | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1890 | ID1890 | Performance M4 | -15 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1891 | ID1891 | Performance M5 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1892 | ID1892 | Performance M6 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1893 | ID1893 | Performance M7 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1894 | ID1894 | Performance M8 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1895 | ID1895 | Performance M9 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1896 | ID1896 | Performance M10 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1897 | ID1897 | Performance M11 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1898 | ID1898 | Performance M12 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1899 | ID1899 | Performance M13 | 63 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1900 | ID1900 | Performance M14 | 66 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1901 | ID1901 | Performance M15 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1902 | ID1902 | Performance M16 | 10 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1903 | ID1903 | Performance M17 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1904 | ID1904 | Performance M18 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1905 | ID1905 | Performance M19 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1906 | ID1906 | Performance M20 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1907 | ID1907 | Performance M21 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1908 | ID1908 | Performance M22 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1909 | ID1909 | Performance M23 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1910 | ID1910 | Performance M24 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1911 | ID1911 | Performance M25 | 63 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1912 | ID1912 | Performance M26 | 66 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1913 | ID1913 | Performance M27 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1914 | ID1914 | Performance M28 | 10 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1915 | ID1915 | Performance M29 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1916 | ID1916 | Performance M30 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1917 | ID1917 | Performance M31 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1918 | ID1918 | Performance M32 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1919 | ID1919 | Performance M33 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1920 | ID1920 | Performance M34 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1921 | ID1921 | Performance M35 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1922 | ID1922 | Performance M36 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1923 | ID1923 | Performance M37 | 63 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1924 | ID1924 | Performance M38 | 66 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1925 | ID1925 | Performance M39 | Med | LOW LOW | HIGH | 0 | YES | NC/OFF, Low low, low, mid, high | 0 | R&D
1926 | ID1926 | Performance M40 | 10 | -20 | 20 | 0 | YES | 1 | 0 | R&D
1927 | ID1927 | Performance M41 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1928 | ID1928 | Performance M42 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1929 | ID1929 | Performance M43 | ON | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1930 | ID1930 | Performance M44 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1931 | ID1931 | Performance M45 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1932 | ID1932 | Performance M46 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1933 | ID1933 | Performance M47 | OFF | ON | OFF | 0 | YES | ON/OFF | 0 | R&D
1934 | ID1934 | Performance M48 | 10 | 0 | 19 | 0 | YES | 1 | 0 | R&D
1935 | ID1935 | ADP 1 | 5 | -20 | 50 | 0 | YES | 0.1 | 0 | R&D
1936 | ID1936 | ADP 2 | 5 | -20 | 50 | 0 | YES | 0.1 | 0 | R&D
1937 | ID1937 | ADP 3 | 6.1 | -20 | 50 | 0 | YES | 0.1 | 0 | R&D
1938 | ID1938 | ADP 4 | 7.2 | -20 | 50 | 0 | YES | 0.1 | 0 | R&D
1939 | ID1939 | ADP 5 | 8.4 | -20 | 50 | 0 | YES | 0.1 | 0 | R&D
1940 | ID1940 | ADP 6 | 9.5 | -20 | 50 | 0 | YES | 0.1 | 0 | R&D
1941 | ID1941 | ADP 7 | 10.6 | -20 | 50 | 0 | YES | 0.1 | 0 | R&D
1942 | ID1942 | ADP 8 | 11.8 | -20 | 50 | 0 | YES | 0.1 | 0 | R&D
1943 | ID1943 | ADP 9 | 12.9 | -20 | 50 | 0 | YES | 0.1 | 0 | R&D
1944 | ID1944 | ADP 10 | 13.9 | -20 | 50 | 0 | YES | 0.1 | 0 | R&D
1945 | ID1945 | ADP 11 | 15 | -20 | 50 | 0 | YES | 0.1 | 0 | R&D
1946 | ID1946 | ADP 12 | 16.1 | -20 | 50 | 0 | YES | 0.1 | 0 | R&D
1947 | ID1947 | ADP 13 | 17.2 | -20 | 50 | 0 | YES | 0.1 | 0 | R&D
1948 | ID1948 | ADP 14 | 18.2 | -20 | 50 | 0 | YES | 0.1 | 0 | R&D
1949 | ID1949 | ADP 15 | 18.2 | -20 | 50 | 0 | YES | 0.1 | 0 | R&D
1950 | ID1950 | ADP Tliq 1 | -1 | -10 | 10 | 0 | YES | 1 | 0 | R&D
1951 | ID1951 | ADP Tliq 2 | 2 | -10 | 10 | 0 | YES | 1 | 0 | R&D
1952 | ID1952 | Cold Draft Prev 1 | 40 | 25 | 45 | 0 | YES | 1 | 0 | R&D
1953 | ID1953 | Cold Draft Prev 2 | 38 | 25 | 45 | 0 | YES | 1 | 0 | R&D
1954 | ID1954 | Gas Shortage ON ΔTcoil | <9 | -10 | 20 | 0 | YES | 1 | 0 | R&D
1955 | ID1955 | Gas Shortage ON EXV | 480 | 0 | 480 | 0 | YES | 1 | 0 | R&D
1956 | ID1956 | Gas Shortage OFF EXV | 450 | 0 | 480 | 0 | YES | 1 | 0 | R&D
1957 | ID1957 | Gas Shortage OFF DCL | 0 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1958 | ID1958 | Gas Short Heat ON ΔTcoil | <3 | -10 | 20 | 0 | YES | 1 | 0 | R&D
1959 | ID1959 | Gas Short Heat ON EXV | 480 | 0 | 480 | 0 | YES | 1 | 0 | R&D
1960 | ID1960 | Gas Short Heat OFF EXV | 450 | 0 | 480 | 0 | YES | 1 | 0 | R&D
1961 | ID1961 | Gas Short Heat OFF TOC | 0 | 0 | 100 | 0 | YES | 1 | 0 | R&D
1962 | ID1962 | UNLV Time | 180 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
1963 | ID1963 | UNLV LP 1 | 34 psig | 0 | 100 | 0 | YES | 1 | 0 | R&D
1964 | ID1964 | UNLV LP 1 Detect Time | 3 sec | 0 | 100 | 0 | YES | 1 | 0 | R&D
1965 | ID1965 | UNLV LP 1 ON Time | 60 sec | 0 | 600 | 0 | YES | 1 | 0 | R&D
1966 | ID1966 | UNLV LP 2 | 39 psig | 0 | 100 | 0 | YES | 1 | 0 | R&D
1967 | ID1967 | Frozen Pro TSC | 2.8 KW | 0 | 150 | 0 | YES | 0.1 | 0 | R&D
1968 | ID1968 | High Cut Pro TSC | 2.8 KW | 0 | 150 | 0 | YES | 0.1 | 0 | R&D
1969 | ID1969 | Cap Unload Pro | 6 KW | 0 | 150 | 0 | YES | 0.1 | 0 | R&D
1970 | ID1970 | High Cut Pro TSC | 2.8 KW | 0 | 150 | 0 | YES | 0.1 | 0 | R&D
1971 | ID1971 | CCH Temp | 20 | 0 | 50 | 0 | YES | 1 | 0 | R&D
1972 | ID1972 | CCH Time | 5 min | 0 | 60 | 0 | YES | 1 | 0 | R&D
1973 | ID1973 | IDBack ECC | 0.6 | 0 | 1 | 0 | YES | 0.1 | 0 | R&D
1974 | ID1974 | IDBack Current R | 1.4 | 0 | 2 | 0 | YES | 0.1 | 0 | R&D
1975 | ID1975 | IDBack DLT R | 1.4 | 0 | 2 | 0 | YES | 0.1 | 0 | R&D
1976 | ID1976 | IDBack Oil | 50% | 0 | 100 | 0 | YES | 1 | 0 | R&D
1977 | ID1977 | IDBack SSH | 10 | 0 | 20 | 0 | YES | 1 | 0 | R&D
1978 | ID1978 | IDBack Sum Cap | 10% | 0 | 100 | 0 | YES | 1 | 0 | R&D
1979 | ID1979 | Auto Fault X1 | 0 | 0 | 150 | 0 | YES | 1 | 0 | R&D
1980 | ID1980 | Auto Fault X2 | -15 | -30 | 100 | 0 | YES | 1 | 0 | R&D
1981 | ID1981 | Auto Fault X3 | 0 | -30 | 100 | 0 | YES | 1 | 0 | R&D
1982 | ID1982 | Auto Fault X4 | -15 | -30 | 100 | 0 | YES | 1 | 0 | R&D
1983 | ID1983 | Auto Fault X5 | 0 | -30 | 100 | 0 | YES | 1 | 0 | R&D
1984 | ID1984 | Auto Fault X6 | -20 | -30 | 100 | 0 | YES | 1 | 0 | R&D
1985 | ID1985 | Auto Fault Y1 | 130 | 0 | 150 | 0 | YES | 1 | 0 | R&D
1986 | ID1986 | Auto Fault Y2 | 50 | -30 | 100 | 0 | YES | 1 | 0 | R&D
1987 | ID1987 | Auto Fault Y3 | 66 | -30 | 100 | 0 | YES | 1 | 0 | R&D
1988 | ID1988 | Auto Fault Y4 | 50 | -30 | 100 | 0 | YES | 1 | 0 | R&D
1989 | ID1989 | Auto Fault Y5 | 66 | -30 | 100 | 0 | YES | 1 | 0 | R&D
1990 | ID1990 | Auto Fault Y6 | 66 | -30 | 100 | 0 | YES | 1 | 0 | R&D
1991 | ID1991 | Auto Fault HPS A | 1 | -10 | 10 | 0 | YES | 0.1 | 0 | R&D
1992 | ID1992 | Auto Fault HPS B | 1 | -10 | 10 | 0 | YES | 0.1 | 0 | R&D
1993 | ID1993 | Auto Fault HPS C | 1 | -10 | 10 | 0 | YES | 0.1 | 0 | R&D
1994 | ID1994 | Auto Fault HPS D | 1 | -10 | 10 | 0 | YES | 0.1 | 0 | R&D
1995 | ID1995 | Auto Fault HPS Ah | 1 | -10 | 10 | 0 | YES | 0.1 | 0 | R&D
1996 | ID1996 | Auto Fault HPS Bh | 1 | -10 | 10 | 0 | YES | 0.1 | 0 | R&D
1997 | ID1997 | Auto Fault HPS Ch | 1 | -10 | 10 | 0 | YES | 0.1 | 0 | R&D
1998 | ID1998 | Auto Fault HPS Dh | 1 | -10 | 10 | 0 | YES | 0.1 | 0 | R&D
1999 | ID1999 | 4 Way Fault A1 | 1 min | 0 | 30 | 0 | YES | 1 | 0 | R&D
2000 | ID2000 | 4 Way Fault A2 | 2 min | 0 | 30 | 0 | YES | 1 | 0 | R&D
2001 | ID2001 | 4 Way Fault A3 | 1 min | 0 | 30 | 0 | YES | 1 | 0 | R&D
2002 | ID2002 | 4 Way Fault A4 | 2 min | 0 | 30 | 0 | YES | 1 | 0 | R&D
2003 | ID2003 | 4 Way Fault B1 | 10 | -10 | 30 | 0 | YES | 1 | 0 | R&D
2004 | ID2004 | 4 Way Fault B2 | 10 | -10 | 30 | 0 | YES | 1 | 0 | R&D
2005 | ID2005 | EXV Fault Open Step | 5 step | 0 | 480 | 0 | YES | 1 | 0 | R&D
2006 | ID2006 | EXV Fault Open Dec | 1 | 0 | 50 | 0 | YES | 1 | 0 | R&D
2007 | ID2007 | EXV Fault Close Step | 5 step | 0 | 480 | 0 | YES | 1 | 0 | R&D
2008 | ID2008 | EXV Fault Close Dec | 1 | 0 | 50 | 0 | YES | 1 | 0 | R&D
2009 | ID2009 | Sensor Fault Time | 30 sec | 0 | 300 | 0 | YES | 1 | 0 | R&D
2010 | ID2010 | Low DSH Cool Time | 300 sec | 0 | 900 | 0 | YES | 1 | 0 | R&D
2011 | ID2011 | Low DSH Heat Time | 300 sec | 0 | 900 | 0 | YES | 1 | 0 | R&D